## Summary
Heat Network Sizing Tool for 480 Properties
Dwelling Peak DHW | 40 | Kw |  | Peak DHW Load | 1000.6874 | kW | 4.332 | l/s | Cost of Pipework | 74305.4667
Dwelling Peak CH | 3 | Kw |  | Peak CH Load | 1080 | kW | 7.3469 | l/s
DP across load (HIU+meter) | 65 | kPa |  | Peak Load | 2028.9374 | kW | 11.3269 | l/s
Peak Load Flow Temperature | 80 | C
Summer Flow Temperature | 65 | C |  | Peak Load Heat Loss | 49.8365 | kW | 2.456%
Return DHW | 25 | C
Return CH | 45 | C |  | Peak Pressure Drop | 188.0387 | kPa
Occupants per property | 3 |  |  | Summer Peak Pressure Drop | 181.2269 | kPa
Flush Rate (HIU function) | 20 | l/m
Peak continuous velocity | 1 | m/s |  | Peak Pressure Drop, Building | 128.7247 | kPa
Fixed DHW/property/day | 50 | litres | info | Summer Peak Pressure Drop, Building | 159.041 | kPa
DHW/person/day | 25 | litres
DHW Temp Rise (for above) | 40 | C |  | Peak Erosion Velocity | 0.79626 | m/s | 1 | m/s max.
Hours Central Heating per Year | 750 | hours |  | Minimum Velocity | 0.50125 | m/s | 0.5 | m/s min.
Insulation Thickness | 40 | mm
Thermal Integration Ltd.
0845 2411441
www.heatweb.com
Note on C8: Peak output temperature from plantroom at -10C external weather conditions, location adjusted.
Note on C10: Based on mains at 15C

## Pipe Sizing
| Example for index flat on 480 property scheme, with 10 risers, feeding 4 storey buildings | [39 empty] | Columns W,X,Y for Herz Williams Pressure Loss Calculation
[7 empty] | Physical |  |  |  |  | Loading | [21 empty] | Pipe Selection |  |  |  | Pressure Loss | [8 empty] | Volume |  | Velocity |  |  |  |  | Thermal Losses | [8 empty] | Summer Figures
ID | Description | Class | Properties | Occupants | Daily | Peak | Length | Elbow | Elbow | Tee | Tee | Count | Total | Danish | DHW | DHW | Min | Est | Htg | Htg | DHW | Htg | DHW | Peak % | Htg | Htg | Htg % | Htg % | Total | Total | Primary | Pipe Area | Pipe Bore | Pipe Bore | Pipe Size | Material | Roughness | f = friction (mm H20 per 100 m pipe) | f = friction (kPa per 100 m pipe) | Head loss (mm H20) | kPa | Pa/m | Equiv | kPa | kPa | kPa | Area | Volume | Peak | Continuous | Weighed | Flush | Accumulative | Thermal | Peak | Peak | Standby | % Time | Standby | Standby | Average | % Share | DHW | f = friction (mm H20 per 100 m pipe) | f = friction (kPa per 100 m pipe) | Head loss (mm H20) | kPa | Pa/m | kPa | kPa | Peak | Continuous | Weighed | Tube | Tube
[5 empty] | DHW | Target | m | 90° | 45° | Line | Branch |  | Length | DHW | Diversity | kW | HIUs | Taps | Diversity | kw | Priority | kw | litre/s | time at | litre/s | litre/s | of Peak | of Daily | Peak | Peak | Return | mm2 | Calculated | Selected | [6 empty] | pipes |  | Length | fittings | TOTAL | Share |  | litres | Velocity | Velocity | Erosion | time | Flush time | Loss | Losses | Losses | Temp | Standby | Losses | Losses | Losses | Losses | litres/s |  |  |  | pipes |  | fittings | TOTAL | Velocity | Velocity | Erosion | Cost | Cost
[5 empty] | kWh | Velocity | [7 empty] | DS439 |  |  | Running | Running |  |  | Saving | NET |  | Peak | peak | minus | Flow | kWh | kW | litre/s | Temp |  |  | mm | mm | [7 empty] | fittings | [5 empty] | m/s | m/s | Velocity | seconds | seconds | W/m/K | kW | kW | C |  | kW | kW | kW |  | Summer | [7 empty] | m/s | m/s | Velocity | £/m | £
[6 empty] | m/s | [7 empty] | kW | [6 empty] | kW |  |  |  |  | priority |  |  |  |  | C | [19 empty] | m/s |  |  |  |  | TOTAL |  |  |  | TOTAL | TOTAL | [11 empty] | m/s
3926.0301
1F | Run to 1st riser | Flow | 480 | 1440 | 2800 | 1.3 | 100 | 4 |  | 1 |  | 1 | 100 | 1000.6874 | 0.052119 | 1000.6874 | 23 | 83.3906 | 0.75 | 1080 | 51.75 | 1028.25 | 4.332 | 11.66% | 7.3469 | 6.9949 | 61.75% | 89.81% | 2028.9374 | 11.3269 | 37.351 | 8712.983 | 105.3267 | 147 | 150 | Steel | 140 | 325.7294 | 3.1954 | 325.7294 | 3.1954 | 31.9541 | 20.58 | 0.65761 | 3.853 | 2.049% | 16971.6546 | 1697.1655 | 0.6674 | 0.43289 | 0.46635 | 5091.4964 | 11778.0904 | 0.49978 | 2.7488 | 2.7488 | 70 | 50% | 2.249 | 2.249 | 2.4989 | 6.393% | 5.9565 | 99.066 | 0.97184 | 99.066 | 0.97184 | 9.7184 | 0.2 | 1.1718 | 0.25525 | 0 | 0.087154 | 50 | 5000
2F | Run to 2nd Riser | Flow | 432 | 1296 | 2520 | 1.3 | 30 |  | 2 | 1 |  | 1 | 30 | 922.4307 | 0.053381 | 922.4307 | 21 | 76.8692 | 0.8 | 1036.8 | 50.4 | 986.4 | 3.9932 | 11.38% | 7.0531 | 6.7102 | 62.69% | 90.38% | 1908.8307 | 10.7034 | 37.5384 | 8233.3926 | 102.387 | 147 | 150 | Steel | 140 | 293.3053 | 2.8773 | 87.9916 | 0.8632 | 28.7732 | 7.644 | 0.21994 | 1.0831 | 0.576% | 16971.6546 | 509.1496 | 0.63066 | 0.41558 | 0.44533 | 1527.4489 | 6686.594 | 0.49978 | 0.82463 | 0.82463 | 70 | 0% | 0.6747 | 0.6747 | 0.82463 | 2.11% | 5.4907 | 85.198 | 0.83579 | 25.5594 | 0.25074 | 8.3579 | 0.063888 | 0.31463 | 0.23529 | 0 | 0.079383 | 50 | 1500
3F | Run to 3rd Riser | Flow | 384 | 1152 | 2240 | 1.3 | 30 |  | 2 | 1 |  | 1 | 30 | 842.9633 | 0.05488 | 842.9633 | 19 | 70.2469 | 0.8 | 921.6 | 45.6 | 876 | 3.6492 | 11.07% | 6.2694 | 5.9592 | 62.02% | 90.37% | 1718.9633 | 9.6084 | 37.4041 | 7391.0579 | 97.0082 | 147 | 150 | Steel | 140 | 240.1666 | 2.356 | 72.05 | 0.70681 | 23.5603 | 7.644 | 0.1801 | 0.88691 | 0.4717% | 16971.6546 | 509.1496 | 0.56614 | 0.3694 | 0.39603 | 1527.4489 | 5159.1451 | 0.49978 | 0.82463 | 0.82463 | 70 | 0% | 0.6747 | 0.6747 | 0.82463 | 2.11% | 5.0176 | 72.1057 | 0.70736 | 21.6317 | 0.21221 | 7.0736 | 0.05407 | 0.26628 | 0.21502 | 0 | 0.071546 | 50 | 1500
4F | Run to 4th Riser | Flow | 336 | 1008 | 1960 | 1.3 | 30 |  | 2 | 1 |  | 1 | 30 | 762.0497 | 0.0567 | 762.0497 | 17 | 63.5041 | 0.8 | 806.4 | 40.8 | 765.6 | 3.2989 | 10.72% | 5.4857 | 5.2082 | 61.22% | 90.36% | 1527.6497 | 8.5071 | 37.2443 | 6543.9074 | 91.2796 | 97 | 100 | Steel | 140 | 1448.9151 | 14.2139 | 434.6745 | 4.2642 | 142.1386 | 5.044 | 0.71695 | 4.9811 | 2.649% | 7389.8051 | 221.6942 | 1.1512 | 0.74234 | 0.79626 | 665.0825 | 3631.6962 | 0.36344 | 0.59968 | 0.59968 | 70 | 0% | 0.49065 | 0.49065 | 0.59968 | 1.534% | 4.536 | 452.1158 | 4.4353 | 135.6347 | 1.3306 | 44.3526 | 0.22371 | 1.5543 | 0.44641 | 0 | 0.14614 | 33.3333 | 1000
5F | Run to 5th Riser | Flow | 288 | 864 | 1680 | 1.3 | 30 |  | 2 | 1 |  | 1 | 30 | 679.3666 | 0.058973 | 679.3666 | 16 | 56.6139 | 0.85 | 734.4 | 40.8 | 693.6 | 2.941 | 10.3% | 4.9959 | 4.7184 | 61.6% | 90.83% | 1372.9666 | 7.6593 | 37.3205 | 5891.8063 | 86.6123 | 97 | 100 | Steel | 140 | 1192.9237 | 11.7026 | 357.8771 | 3.5108 | 117.0258 | 5.044 | 0.59028 | 4.1011 | 2.181% | 7389.8051 | 221.6942 | 1.0365 | 0.67606 | 0.72156 | 665.0825 | 2966.6137 | 0.36344 | 0.59968 | 0.59968 | 70 | 0% | 0.49065 | 0.49065 | 0.59968 | 1.534% | 4.0438 | 365.4884 | 3.5854 | 109.6465 | 1.0756 | 35.8544 | 0.18085 | 1.2565 | 0.39798 | 0 | 0.12775 | 33.3333 | 1000
6F | Run to 6th Riser | Flow | 240 | 720 | 1400 | 1.3 | 30 |  | 2 | 1 |  | 1 | 30 | 594.4483 | 0.061922 | 594.4483 | 14 | 49.5374 | 0.85 | 612 | 35.7 | 576.3 | 2.5734 | 9.813% | 4.1633 | 3.9204 | 60.37% | 90.81% | 1170.7483 | 6.4938 | 37.0744 | 4995.2136 | 79.7503 | 97 | 100 | Steel | 140 | 878.6879 | 8.6199 | 263.6064 | 2.586 | 86.1993 | 5.044 | 0.43479 | 3.0208 | 1.606% | 7389.8051 | 221.6942 | 0.87875 | 0.56338 | 0.60169 | 665.0825 | 2301.5313 | 0.36344 | 0.59968 | 0.59968 | 70 | 0% | 0.49065 | 0.49065 | 0.59968 | 1.534% | 3.5384 | 285.4145 | 2.7999 | 85.6243 | 0.83997 | 27.9992 | 0.14123 | 0.9812 | 0.34823 | 0 | 0.10909 | 33.3333 | 1000
7F | Run to 7th Riser | Flow | 192 | 576 | 1120 | 1.3 | 30 |  | 2 | 1 |  | 1 | 30 | 506.5804 | 0.065961 | 506.5804 | 12 | 42.215 | 0.85 | 489.6 | 30.6 | 459 | 2.193 | 9.212% | 3.3306 | 3.1224 | 58.74% | 90.77% | 965.5804 | 5.3154 | 36.7486 | 4088.7984 | 72.1528 | 97 | 100 | Steel | 140 | 606.4399 | 5.9492 | 181.932 | 1.7848 | 59.4918 | 5.044 | 0.30008 | 2.0848 | 1.109% | 7389.8051 | 221.6942 | 0.71929 | 0.4507 | 0.48175 | 665.0825 | 1636.4488 | 0.36344 | 0.59968 | 0.59968 | 70 | 0% | 0.49065 | 0.49065 | 0.59968 | 1.534% | 3.0154 | 212.2392 | 2.0821 | 63.6717 | 0.62462 | 20.8207 | 0.10502 | 0.72964 | 0.29676 | 0 | 0.090071 | 33.3333 | 1000
8F | Run to 8th Riser | Flow | 144 | 432 | 840 | 1.3 | 30 |  | 2 | 1 |  | 1 | 30 | 414.56 | 0.071972 | 414.56 | 10 | 34.5467 | 0.9 | 388.8 | 27 | 361.8 | 1.7946 | 8.443% | 2.6449 | 2.4612 | 57.83% | 91.18% | 776.36 | 4.2559 | 36.5663 | 3273.7358 | 64.562 | 72 | 75 | Steel | 140 | 1713.0102 | 16.8046 | 513.903 | 5.0414 | 168.0463 | 3.744 | 0.62917 | 5.6706 | 3.016% | 4071.5006 | 122.145 | 1.0453 | 0.64961 | 0.69182 | 366.4351 | 971.3664 | 0.29428 | 0.48556 | 0.48556 | 70 | 0% | 0.39727 | 0.39727 | 0.48556 | 1.242% | 2.4676 | 624.2738 | 6.1241 | 187.2821 | 1.8372 | 61.2413 | 0.22929 | 2.0665 | 0.44078 | 0 | 0.12807 | 25 | 750
9F | Run to 9th Riser | Flow | 96 | 288 | 560 | 1.3 | 30 |  | 2 | 1 |  | 1 | 30 | 316.0416 | 0.082303 | 316.0416 | 8 | 26.3368 | 0.9 | 259.2 | 21.6 | 237.6 | 1.3681 | 7.383% | 1.7633 | 1.6163 | 54.16% | 91.06% | 553.6416 | 2.9845 | 35.8316 | 2295.7478 | 54.0651 | 72 | 75 | Steel | 140 | 887.8318 | 8.7096 | 266.3495 | 2.6129 | 87.0963 | 3.744 | 0.32609 | 2.939 | 1.563% | 4071.5006 | 122.145 | 0.73302 | 0.43308 | 0.46193 | 366.4351 | 604.9313 | 0.29428 | 0.48556 | 0.48556 | 70 | 0% | 0.39727 | 0.39727 | 0.48556 | 1.242% | 1.8812 | 377.685 | 3.7051 | 113.3055 | 1.1115 | 37.0509 | 0.13872 | 1.2502 | 0.33603 | 0 | 0.091305 | 25 | 750
10F | Run to 10th riser (ground floor) | Flow | 48 | 144 | 280 | 1.3 | 30 | 1 | 2 |  |  | 1 | 30 | 204.9702 | 0.10676 | 204.9702 | 5 | 17.0809 | 0.9 | 129.6 | 13.5 | 116.1 | 0.88732 | 5.692% | 0.88163 | 0.7898 | 47.09% | 90.87% | 321.0702 | 1.6771 | 34.4185 | 1290.0868 | 40.5289 | 51 | 54 | Copper | 140 | 1634.6847 | 16.0363 | 490.4054 | 4.8109 | 160.3626 | 3.162 | 0.50707 | 5.3179 | 2.828% | 2042.8189 | 61.2846 | 0.82098 | 0.43158 | 0.46262 | 183.8537 | 238.4963 | 0.23505 | 0.38783 | 0.38783 | 70 | 0% | 0.31732 | 0.31732 | 0.38783 | 0.9922% | 1.2201 | 906.8243 | 8.8959 | 272.0473 | 2.6688 | 88.9595 | 0.28129 | 2.9501 | 0.43436 | 0 | 0.10363 | 17.4667 | 524
11F | Riser to 1st floor | Flow | 36 | 108 | 210 | 1.5 | 4 |  |  | 1 |  | 10 | 40 | 173.24 | 0.12031 | 173.24 | 4 | 14.4367 | 0.95 | 102.6 | 11.4 | 91.2 | 0.74996 | 5.051% | 0.69796 | 0.62041 | 45.27% | 91.25% | 264.44 | 1.3704 | 34.0546 | 913.5766 | 34.1058 | 39 | 42 | Copper | 140 | 4147.851 | 40.6904 | 165.914 | 1.6276 | 406.9042 | 0.78 | 0.31739 | 1.945 | 1.034% | 1194.5896 | 4.7784 | 1.1471 | 0.58427 | 0.62497 | 14.3351 | 54.6426 | 0.20033 | 0.044074 | 0.44074 | 70 | 1% | 0.03606 | 0.3606 | 0.43993 | 1.125% | 1.0312 | 2449.6616 | 24.0312 | 97.9865 | 0.96125 | 240.3118 | 0.18744 | 1.1487 | 0.62779 | 0 | 0.14109 | 13.3933 | 535.7333
12F | Riser to 2nd floor | Flow | 24 | 72 | 140 | 1.75 | 4 |  |  | 1 |  | 10 | 40 | 138.2608 | 0.14402 | 138.2608 | 4 | 11.5217 | 0.95 | 68.4 | 11.4 | 57 | 0.59853 | 4.219% | 0.46531 | 0.38776 | 39.31% | 90.72% | 195.2608 | 0.98629 | 32.8629 | 563.5924 | 26.7878 | 32.6 | 35 | Copper | 140 | 5395.8643 | 52.9334 | 215.8346 | 2.1173 | 529.3343 | 0.652 | 0.34513 | 2.4625 | 1.31% | 834.689 | 3.3388 | 1.1816 | 0.55746 | 0.59713 | 10.0163 | 40.3075 | 0.17958 | 0.039508 | 0.39508 | 70 | 2% | 0.032325 | 0.32325 | 0.39364 | 1.007% | 0.82298 | 3858.949 | 37.8563 | 154.358 | 1.5143 | 378.5629 | 0.24682 | 1.7611 | 0.71707 | 0 | 0.14729 | 10.98 | 439.2
13F | Riser to 3rd floor | Flow | 12 | 36 | 70 | 1.75 | 4 |  |  |  | 1 | 10 | 40 | 97.0051 | 0.20209 | 97.0051 | 3 | 8.0838 | 0.95 | 34.2 | 8.55 | 25.65 | 0.41994 | 3.007% | 0.23265 | 0.17449 | 29.35% | 89.79% | 122.6551 | 0.59443 | 30.8709 | 339.6716 | 20.7962 | 26 | 28 | Copper | 140 | 6350.4239 | 62.2977 | 254.017 | 2.4919 | 622.9766 | 1.56 | 0.97184 | 3.4637 | 1.842% | 530.9287 | 2.1237 | 1.1196 | 0.4382 | 0.47322 | 6.3711 | 30.2912 | 0.15825 | 0.034815 | 0.34815 | 70 | 3% | 0.028485 | 0.28485 | 0.34625 | 0.8858% | 0.57741 | 6017.905 | 59.0356 | 240.7162 | 2.3614 | 590.3565 | 0.92096 | 3.2824 | 0.79095 | 0 | 0.13715 | 5.7133 | 228.5333
14F | Lateral | Periphery | 6 | 18 | 35 | 1.5 | 10 |  |  | 1 |  | 80 | 800 | 70.7904 | 0.35 | 84 | 3 | 7 | 1 | 18 | 9 | 9 | 0.36364 | 1.736% | 0.12245 | 0.061224 | 14.41% | 86.06% | 93 | 0.42486 | 27.8821 | 283.2406 | 18.9904 | 20 | 22 | Copper | 140 | 12220.2134 | 119.8803 | 1222.0213 | 11.988 | 1198.8029 | 0.4 | 0.47952 | 12.4676 | 6.63% | 314.159 | 3.1416 | 1.3524 | 0.38977 | 0.42548 | 9.4248 | 23.9201 | 0.13927 | 0.076597 | 6.1278 | 25 | 10% | 0 | 0 | 5.515 | 14.11% | 0.5 | 16521.8364 | 162.0792 | 1652.1836 | 16.2079 | 1620.7922 | 0.64832 | 16.8562 | 1.1575 | 0 | 0.15251 | 4.4867 | 3589.3333
15F | Lateral | Periphery | 4 | 12 | 23.3333 | 1.5 | 6 |  |  | 1 |  | 80 | 480 | 59.96 | 0.5 | 80 | 2 | 6.6667 | 1 | 12 | 6 | 6 | 0.34632 | 1.215% | 0.081633 | 0.040816 | 10.54% | 86.06% | 86 | 0.38714 | 27.1086 | 258.0911 | 18.1277 | 20 | 22 | Copper | 140 | 10287.0436 | 100.9159 | 617.2226 | 6.055 | 1009.159 | 0.4 | 0.40366 | 6.4586 | 3.435% | 314.159 | 1.885 | 1.2323 | 0.25985 | 0.29181 | 5.6549 | 14.4953 | 0.13927 | 0.045958 | 3.6767 | 25 | 15% | 0 | 0 | 3.1252 | 7.995% | 0.47619 | 15094.3959 | 148.076 | 905.6638 | 8.8846 | 1480.7602 | 0.5923 | 9.4769 | 1.1024 | 0 | 0.12153 | 4.4867 | 2153.6
16F | Lateral | Periphery | 2 | 6 | 11.6667 | 1.5 | 6 |  |  |  | 1 | 80 | 480 | 46.5672 | 0.8 | 64 | 2 | 5.3333 | 1 | 6 | 6 | 0 | 0.27706 | 0.7595% | 0.040816 | 0 | 0% | 0% | 64 | 0.27706 | 25 | 184.7042 | 15.3353 | 20 | 22 | Copper | 140 | 5536.0728 | 54.3089 | 332.1644 | 3.2585 | 543.0887 | 1.2 | 0.65171 | 3.9102 | 2.079% | 314.159 | 1.885 | 0.8819 | 0.12992 | 0.15053 | 5.6549 | 8.8404 | 0.13927 | 0.045958 | 3.6767 | 25 | 20% | 0 | 0 | 2.9413 | 7.525% | 0.38095 | 9984.7775 | 97.9507 | 599.0867 | 5.877 | 979.5067 | 1.1754 | 7.0524 | 0.8819 | 0 | 0.076859 | 4.4867 | 2153.6
18F | Feed | Periphery | 1 | 3 | 5.8333 | 2 | 8 | 5 |  |  |  | 480 | 3840 | 37.59 | 1 | 40 | 1 | 3.3333 | 1 | 3 | 3 | 0 | 0.17316 | 0.6076% | 0.020408 | 0 | 0% | 0% | 40 | 0.17316 | 25 | 86.5801 | 10.4994 | 13 | 15 | Copper | 140 | 18855.6562 | 184.974 | 1508.4525 | 14.7979 | 1849.7399 | 1.95 | 3.607 | 18.4049 | 9.788% | 132.7322 | 1.0619 | 1.3046 | 0.15375 | 0.18395 | 3.1856 | 3.1856 | 0.11573 | 0.050923 | 24.4432 | 25 | 35% | 0 | 0 | 15.8881 | 40.64% | 0.2381 | 34007.7773 | 333.6163 | 2720.6222 | 26.6893 | 3336.163 | 6.5055 | 33.1948 | 1.3046 | 0 | 0.10169 | 2.0933 | 8038.4
HIU | Load | Load | 1 | 3 | 5.8333 | [6 empty] | 480 |  | 37.59 | 1 | 40 | 1 | 3.3333 | 1 | 3 | 3 | 0 | 0.17316 | 0.6076% | 0.020408 | 0 | 0% | 0% | 40 | 0.17316 | 25 | [13 empty] | 65 | 34.57% | [16 empty] | 0.2381 |  |  | 0 |  |  |  | 65
1F | Run to 1st riser | Return | 480 | 1440 | 2800 | 1 | 100 | 4 | 0 | 1 | 0 | 1 | 100 | 1000.6874 | 0.052119 | 1000.6874 | 23 | 83.3906 | 0.75 | 1080 | 51.75 | 1028.25 | 4.332 | 11.66% | 7.3469 | 6.9949 | 61.75% | 89.81% | 2028.9374 | 11.3269 | 37.351 | 11326.8779 | 120.091 | 147 | 150 | Steel | 140 | 325.7294 | 3.1954 | 325.7294 | 3.1954 | 31.9541 | 20.58 | 0.65761 | 3.853 | 2.049% | 16971.6546 | 1697.1655 | 0.6674 | 0.43289 | 0.46635 |  |  | 0.49978 | 0.61727 | 0.61727 | 50 | 0% | 1.2494 | 1.2494 | 0.61727 | 1.579% | 5.9565 | 99.066 | 0.97184 | 99.066 | 0.97184 | 9.7184 | 0.2 | 1.1718 | 0.25525 | 0 | 0.087154 | 50 | 5000
2F | Run to 2nd Riser | Return | 432 | 1296 | 2520 | 1 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 922.4307 | 0.053381 | 922.4307 | 21 | 76.8692 | 0.8 | 1036.8 | 50.4 | 986.4 | 3.9932 | 11.38% | 7.0531 | 6.7102 | 62.69% | 90.38% | 1908.8307 | 10.7034 | 37.5384 | 10703.4104 | 116.7391 | 147 | 150 | Steel | 140 | 293.3053 | 2.8773 | 87.9916 | 0.8632 | 28.7732 | 7.644 | 0.21994 | 1.0831 | 0.576% | 16971.6546 | 509.1496 | 0.63066 | 0.41558 | 0.44533 |  |  | 0.49978 | 0.18799 | 0.18799 | 50 | 0% | 0.37483 | 0.37483 | 0.18799 | 0.4809% | 5.4907 | 85.198 | 0.83579 | 25.5594 | 0.25074 | 8.3579 | 0.063888 | 0.31463 | 0.23529 | 0 | 0.079383 | 50 | 1500
3F | Run to 3rd Riser | Return | 384 | 1152 | 2240 | 1 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 842.9633 | 0.05488 | 842.9633 | 19 | 70.2469 | 0.8 | 921.6 | 45.6 | 876 | 3.6492 | 11.07% | 6.2694 | 5.9592 | 62.02% | 90.37% | 1718.9633 | 9.6084 | 37.4041 | 9608.3753 | 110.6064 | 147 | 150 | Steel | 140 | 240.1666 | 2.356 | 72.05 | 0.70681 | 23.5603 | 7.644 | 0.1801 | 0.88691 | 0.4717% | 16971.6546 | 509.1496 | 0.56614 | 0.3694 | 0.39603 |  |  | 0.49978 | 0.18598 | 0.18598 | 50 | 0% | 0.37483 | 0.37483 | 0.18598 | 0.4758% | 5.0176 | 72.1057 | 0.70736 | 21.6317 | 0.21221 | 7.0736 | 0.05407 | 0.26628 | 0.21502 | 0 | 0.071546 | 50 | 1500
4F | Run to 4th Riser | Return | 336 | 1008 | 1960 | 1 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 762.0497 | 0.0567 | 762.0497 | 17 | 63.5041 | 0.8 | 806.4 | 40.8 | 765.6 | 3.2989 | 10.72% | 5.4857 | 5.2082 | 61.22% | 90.36% | 1527.6497 | 8.5071 | 37.2443 | 8507.0797 | 104.0748 | 147 | 150 | Steel | 140 | 191.6895 | 1.8805 | 57.5068 | 0.56414 | 18.8047 | 7.644 | 0.14374 | 0.70789 | 0.3765% | 16971.6546 | 509.1496 | 0.50125 | 0.32323 | 0.34671 |  |  | 0.49978 | 0.18358 | 0.18358 | 50 | 0% | 0.37483 | 0.37483 | 0.18358 | 0.4696% | 4.536 | 59.8143 | 0.58678 | 17.9443 | 0.17603 | 5.8678 | 0.044853 | 0.22089 | 0.19438 | 0 | 0.063632 | 50 | 1500
5F | Run to 5th Riser | Return | 288 | 864 | 1680 | 1.1 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 679.3666 | 0.058973 | 679.3666 | 16 | 56.6139 | 0.85 | 734.4 | 40.8 | 693.6 | 2.941 | 10.3% | 4.9959 | 4.7184 | 61.6% | 90.83% | 1372.9666 | 7.6593 | 37.3205 | 6963.0438 | 94.1575 | 97 | 100 | Steel | 140 | 1192.9237 | 11.7026 | 357.8771 | 3.5108 | 117.0258 | 5.044 | 0.59028 | 4.1011 | 2.181% | 7389.8051 | 221.6942 | 1.0365 | 0.67606 | 0.72156 |  |  | 0.36344 | 0.13433 | 0.13433 | 50 | 0% | 0.27258 | 0.27258 | 0.13433 | 0.3437% | 4.0438 | 365.4884 | 3.5854 | 109.6465 | 1.0756 | 35.8544 | 0.18085 | 1.2565 | 0.39798 | 0 | 0.12775 | 33.3333 | 1000
6F | Run to 6th Riser | Return | 240 | 720 | 1400 | 1 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 594.4483 | 0.061922 | 594.4483 | 14 | 49.5374 | 0.85 | 612 | 35.7 | 576.3 | 2.5734 | 9.813% | 4.1633 | 3.9204 | 60.37% | 90.81% | 1170.7483 | 6.4938 | 37.0744 | 6493.7776 | 90.9293 | 97 | 100 | Steel | 140 | 878.6879 | 8.6199 | 263.6064 | 2.586 | 86.1993 | 5.044 | 0.43479 | 3.0208 | 1.606% | 7389.8051 | 221.6942 | 0.87875 | 0.56338 | 0.60169 |  |  | 0.36344 | 0.13165 | 0.13165 | 50 | 0% | 0.27258 | 0.27258 | 0.13165 | 0.3368% | 3.5384 | 285.4145 | 2.7999 | 85.6243 | 0.83997 | 27.9992 | 0.14123 | 0.9812 | 0.34823 | 0 | 0.10909 | 33.3333 | 1000
7F | Run to 7th Riser | Return | 192 | 576 | 1120 | 1 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 506.5804 | 0.065961 | 506.5804 | 12 | 42.215 | 0.85 | 489.6 | 30.6 | 459 | 2.193 | 9.212% | 3.3306 | 3.1224 | 58.74% | 90.77% | 965.5804 | 5.3154 | 36.7486 | 5315.4379 | 82.2668 | 97 | 100 | Steel | 140 | 606.4399 | 5.9492 | 181.932 | 1.7848 | 59.4918 | 5.044 | 0.30008 | 2.0848 | 1.109% | 7389.8051 | 221.6942 | 0.71929 | 0.4507 | 0.48175 |  |  | 0.36344 | 0.1281 | 0.1281 | 50 | 0% | 0.27258 | 0.27258 | 0.1281 | 0.3277% | 3.0154 | 212.2392 | 2.0821 | 63.6717 | 0.62462 | 20.8207 | 0.10502 | 0.72964 | 0.29676 | 0 | 0.090071 | 33.3333 | 1000
8F | Run to 8th Riser | Return | 144 | 432 | 840 | 1 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 414.56 | 0.071972 | 414.56 | 10 | 34.5467 | 0.9 | 388.8 | 27 | 361.8 | 1.7946 | 8.443% | 2.6449 | 2.4612 | 57.83% | 91.18% | 776.36 | 4.2559 | 36.5663 | 4255.8565 | 73.612 | 97 | 100 | Steel | 140 | 401.7661 | 3.9413 | 120.5298 | 1.1824 | 39.4133 | 5.044 | 0.1988 | 1.3812 | 0.7345% | 7389.8051 | 221.6942 | 0.57591 | 0.35791 | 0.38117 |  |  | 0.36344 | 0.12611 | 0.12611 | 50 | 0% | 0.27258 | 0.27258 | 0.12611 | 0.3226% | 2.4676 | 146.416 | 1.4363 | 43.9248 | 0.4309 | 14.3634 | 0.072449 | 0.50335 | 0.24285 | 0 | 0.070564 | 33.3333 | 1000
9F | Run to 9th Riser | Return | 96 | 288 | 560 | 1 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 316.0416 | 0.082303 | 316.0416 | 8 | 26.3368 | 0.9 | 259.2 | 21.6 | 237.6 | 1.3681 | 7.383% | 1.7633 | 1.6163 | 54.16% | 91.06% | 553.6416 | 2.9845 | 35.8316 | 2984.4721 | 61.6437 | 72 | 75 | Steel | 140 | 887.8318 | 8.7096 | 266.3495 | 2.6129 | 87.0963 | 3.744 | 0.32609 | 2.939 | 1.563% | 4071.5006 | 122.145 | 0.73302 | 0.43308 | 0.46193 |  |  | 0.29428 | 0.095625 | 0.095625 | 50 | 0% | 0.22071 | 0.22071 | 0.095625 | 0.2446% | 1.8812 | 377.685 | 3.7051 | 113.3055 | 1.1115 | 37.0509 | 0.13872 | 1.2502 | 0.33603 | 0 | 0.091305 | 25 | 750
10F | Run to 10th riser (ground floor) | Return | 48 | 144 | 280 | 1 | 30 | 1 | 2 | 0 | 0 | 1 | 30 | 204.9702 | 0.10676 | 204.9702 | 5 | 17.0809 | 0.9 | 129.6 | 13.5 | 116.1 | 0.88732 | 5.692% | 0.88163 | 0.7898 | 47.09% | 90.87% | 321.0702 | 1.6771 | 34.4185 | 1677.1129 | 46.21 | 51 | 54 | Copper | 140 | 1634.6847 | 16.0363 | 490.4054 | 4.8109 | 160.3626 | 3.162 | 0.50707 | 5.3179 | 2.828% | 2042.8189 | 61.2846 | 0.82098 | 0.43158 | 0.46262 |  |  | 0.23505 | 0.066415 | 0.066415 | 25 | 0% | 0 | 0 | 0.066415 | 0.1699% | 1.2201 | 906.8243 | 8.8959 | 272.0473 | 2.6688 | 88.9595 | 0.28129 | 2.9501 | 0.43436 | 0 | 0.10363 | 17.4667 | 524
11F | Riser to 1st floor | Return | 36 | 108 | 210 | 1 | 4 | 0 | 0 | 1 | 0 | 10 | 40 | 173.24 | 0.12031 | 173.24 | 4 | 14.4367 | 0.95 | 102.6 | 11.4 | 91.2 | 0.74996 | 5.051% | 0.69796 | 0.62041 | 45.27% | 91.25% | 264.44 | 1.3704 | 34.0546 | 1370.3649 | 41.7709 | 51 | 54 | Copper | 140 | 1124.5151 | 11.0315 | 44.9806 | 0.44126 | 110.3149 | 1.02 | 0.11252 | 0.55378 | 0.2945% | 2042.8189 | 8.1713 | 0.67082 | 0.34166 | 0.36547 |  |  | 0.23505 | 0.0085132 | 0.085132 | 25 | 1% | 0 | 0 | 0.084281 | 0.2156% | 1.0312 | 664.1226 | 6.515 | 26.5649 | 0.2606 | 65.1504 | 0.066453 | 0.32706 | 0.36712 | 0 | 0.082506 | 17.4667 | 698.6667
12F | Riser to 2nd floor | Return | 24 | 72 | 140 | 1 | 4 | 0 | 0 | 1 | 0 | 10 | 40 | 138.2608 | 0.14402 | 138.2608 | 4 | 11.5217 | 0.95 | 68.4 | 11.4 | 57 | 0.59853 | 4.219% | 0.46531 | 0.38776 | 39.31% | 90.72% | 195.2608 | 0.98629 | 32.8629 | 986.2868 | 35.437 | 39 | 42 | Copper | 140 | 2255.7783 | 22.1292 | 90.2311 | 0.88517 | 221.2918 | 0.78 | 0.17261 | 1.0578 | 0.5625% | 1194.5896 | 4.7784 | 0.82563 | 0.38951 | 0.41723 |  |  | 0.20033 | 0.0063009 | 0.063009 | 25 | 2% | 0 | 0 | 0.061748 | 0.158% | 0.82298 | 1613.2602 | 15.8261 | 64.5304 | 0.63304 | 158.2608 | 0.12344 | 0.75649 | 0.50104 | 0 | 0.10291 | 13.3933 | 535.7333
13F | Riser to 3rd floor | Return | 12 | 36 | 70 | 1 | 4 | 0 | 0 | 0 | 1 | 10 | 40 | 97.0051 | 0.20209 | 97.0051 | 3 | 8.0838 | 0.95 | 34.2 | 8.55 | 25.65 | 0.41994 | 3.007% | 0.23265 | 0.17449 | 29.35% | 89.79% | 122.6551 | 0.59443 | 30.8709 | 594.4253 | 27.5108 | 32.6 | 35 | Copper | 140 | 2112.4931 | 20.7236 | 84.4997 | 0.82894 | 207.2356 | 1.956 | 0.40535 | 1.2343 | 0.6564% | 834.689 | 3.3388 | 0.71215 | 0.27873 | 0.301 |  |  | 0.17958 | 0.0042172 | 0.042172 | 25 | 3% | 0 | 0 | 0.040907 | 0.1046% | 0.57741 | 2001.8794 | 19.6384 | 80.0752 | 0.78554 | 196.3844 | 0.38413 | 1.1697 | 0.5031 | 0 | 0.087238 | 10.98 | 439.2
14F | Lateral | Return | 6 | 18 | 35 | 1 | 10 | 0 | 0 | 1 | 0 | 80 | 800 | 70.7904 | 0.35 | 84 | 3 | 7 | 1 | 18 | 9 | 9 | 0.36364 | 1.736% | 0.12245 | 0.061224 | 14.41% | 86.06% | 93 | 0.42486 | 27.8821 | 424.8609 | 23.2583 | 26 | 28 | Copper | 140 | 3409.4742 | 33.4469 | 340.9474 | 3.3447 | 334.4694 | 0.52 | 0.17392 | 3.5186 | 1.871% | 530.9287 | 5.3093 | 0.80022 | 0.23063 | 0.25176 |  |  | 0.15825 | 0.0045609 | 0.36488 | 25 | 5% | 0 | 0 | 0.34663 | 0.8868% | 0.5 | 4609.6392 | 45.2206 | 460.9639 | 4.5221 | 452.2056 | 0.23515 | 4.7572 | 0.68491 | 0 | 0.090244 | 5.7133 | 4570.6667
15F | Lateral | Return | 4 | 12 | 23.3333 | 1 | 6 | 0 | 0 | 1 | 0 | 80 | 480 | 59.96 | 0.5 | 80 | 2 | 6.6667 | 1 | 12 | 6 | 6 | 0.34632 | 1.215% | 0.081633 | 0.040816 | 10.54% | 86.06% | 86 | 0.38714 | 27.1086 | 387.1367 | 22.2018 | 26 | 28 | Copper | 140 | 2870.1143 | 28.1558 | 172.2069 | 1.6893 | 281.5582 | 0.52 | 0.14641 | 1.8358 | 0.9763% | 530.9287 | 3.1856 | 0.72917 | 0.15375 | 0.17267 |  |  | 0.15825 | 0.0020022 | 0.16017 | 25 | 10% | 0 | 0 | 0.14415 | 0.3688% | 0.47619 | 4211.3793 | 41.3136 | 252.6828 | 2.4788 | 413.1363 | 0.21483 | 2.6936 | 0.65229 | 0 | 0.071908 | 5.7133 | 2742.4
16F | Lateral | Return | 2 | 6 | 11.6667 | 1 | 6 | 0 | 0 | 0 | 1 | 80 | 480 | 46.5672 | 0.8 | 64 | 2 | 5.3333 | 1 | 6 | 6 | 0 | 0.27706 | 0.7595% | 0.040816 | 0 | 0% | 0% | 64 | 0.27706 | 25 | 277.0563 | 18.7819 | 20 | 22 | Copper | 140 | 5536.0728 | 54.3089 | 332.1644 | 3.2585 | 543.0887 | 1.2 | 0.65171 | 3.9102 | 2.079% | 314.159 | 1.885 | 0.8819 | 0.12992 | 0.15053 |  |  | 0.13927 | 0 | 0 | 25 | 20% | 0 | 0 | 0 | 0% | 0.38095 | 9984.7775 | 97.9507 | 599.0867 | 5.877 | 979.5067 | 1.1754 | 7.0524 | 0.8819 | 0 | 0.076859 | 4.4867 | 2153.6
18F | Feed | Return | 1 | 3 | 5.8333 | 1 | 8 | 5 | 0 | 0 | 0 | 480 | 3840 | 37.59 | 1 | 40 | 1 | 3.3333 | 1 | 3 | 3 | 0 | 0.17316 | 0.6076% | 0.020408 | 0 | 0% | 0% | 40 | 0.17316 | 25 | 173.1602 | 14.8484 | 20 | 22 | Copper | 140 | 2318.3104 | 22.7426 | 185.4648 | 1.8194 | 227.4263 | 3 | 0.68228 | 2.5017 | 1.33% | 314.159 | 2.5133 | 0.55119 | 0.064961 | 0.07772 |  |  | 0.13927 | 0 | 0 | 25 | 30% | 0 | 0 | 0 | 0% | 0.2381 | 4181.2697 | 41.0183 | 334.5016 | 3.2815 | 410.1826 | 1.2305 | 4.512 | 0.55119 | 0 | 0.042966 | 4.4867 | 17228.8
[13 empty] | 12180 | [27 empty] | 105.7971 |  |  | 17.2416 | 188.0387 |  |  | 4324.002 | 0.50125 |  | 0.79626 |  |  |  |  | 49.8365 |  |  |  |  | 39.0901 | [8 empty] | 181.2269 |  |  |  |  | 74305.4667
| Dwelling Peak DHW | 40 | Kw | [44 empty] | 8250.0322
| Dwelling Peak CH | 3 | Kw | [41 empty] | Building | [15 empty] | 9.7629 | [8 empty] | Building |  |  |  |  | per property
| DP across load (HIU+meter) | 65 | kPa | [41 empty] | 128.7247 | [15 empty] | on network | [8 empty] | 159.041 |  |  |  |  | 154.8031
| Peak Load Flow Temperature | 80 | C | [41 empty] | kPa | [24 empty] | kPa
| Summer Flow Temperature | 65 | C | [57 empty] | 29.3272
| Return DHW | 25 | C | [57 empty] | in buildings
| Return CH | 45 | C
| Occupants per property | 3
| Flush Rate (HIU function) | 20 | l/m
| Peak continuous velocity | 1 | m/s
| Fixed DHW/property/day | 50 | litres
| DHW/person/day | 25 | litres
| DHW Temp Rise (for above) | 40
| Average tap load | 12 | kW
| DHW Priority (0/1) | 1
http://www.katmarsoftware.com/articles/pipe-fitting-pressure-drop.htm
| Descroption | L/D
| Ball valve, full bore | 3
| Ball valve, reduced bore | 25
| Tee, Inline | 20
| Tee, Branch | 60
| 90° screwed elbow | 30
| 90° long radius bend | 13
| 45° screwed elbow | 16
| 45° long radius bend | 10
Note on H7: Used to select appropriate pipe size.
Note on Q7: For calculation of DHW diversity.
Note on R7: The DHW load used in calculation.
Note on T7: Not used in any calculaton
Note on AQ7: In a real calculation, pressure calculated pressure drops should be checked against pipe manufacturers pressure drop data.
Note on BC7: Green if under 30s. Yellow if under 60s. With HIU keep warm timed, longer delays are allowable. 1 minute initially selected as maximum allowed time waiting outside keep warm times.
Note on BQ7: In a real calculation, pressure calculated pressure drops should be checked against pipe manufacturers pressure drop data.
Note on R24: 10 or above properties and diversity follows a recognised standard.
Note on H25: Lateral set to 1.5 for noise reasons.

## Plantroom Sizing
Hour | EST Volume | % | DHW kWh | Max time at peak diversity | Start | End of DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW
1 | 2.25 | 1.828% | 51.1779 | 5.114% | 0:00 | 0:03 | 70.5721 | 0 | -44.9513 | 195.5721 | 0 | -38.5584 | 320.5721 | 0 | -32.1656 | 420.5721 | 0 | -27.0513 | 570.5721 | 0 | -19.3799 | 670.5721 | 0 | -14.2656
2 | 1.5 | 1.219% | 34.1186 | 3.41% | 1:00 | 1:02 | 87.6314 | 0 | -29.9675 | 212.6314 | 0 | -25.7056 | 337.6314 | 0 | -21.4437 | 437.6314 | 0 | -18.0342 | 587.6314 | 0 | -12.9199 | 687.6314 | 0 | -9.5104
3 | 1.25 | 1.015% | 28.4322 | 2.841% | 2:00 | 2:02 | 93.3178 | 0 | -24.9729 | 218.3178 | 0 | -21.4214 | 343.3178 | 0 | -17.8698 | 443.3178 | 0 | -15.0285 | 593.3178 | 0 | -10.7666 | 693.3178 | 0 | -7.9253
4 | 1 | 0.8123% | 22.7457 | 2.273% | 3:00 | 3:01 | 99.0043 | 0 | -19.9783 | 224.0043 | 0 | -17.1371 | 349.0043 | 0 | -14.2958 | 449.0043 | 0 | -12.0228 | 599.0043 | 0 | -8.6133 | 699.0043 | 0 | -6.3403
5 | 1.6 | 1.3% | 36.3932 | 3.637% | 4:00 | 4:02 | 85.3568 | 0 | -31.9654 | 210.3568 | 0 | -27.4193 | 335.3568 | 0 | -22.8733 | 435.3568 | 0 | -19.2365 | 585.3568 | 0 | -13.7813 | 685.3568 | 0 | -10.1444
6 | 2.1 | 1.706% | 47.766 | 4.773% | 5:00 | 5:03 | 73.984 | 0 | -41.9545 | 198.984 | 0 | -35.9879 | 323.984 | 0 | -30.0212 | 423.984 | 0 | -25.2479 | 573.984 | 0 | -18.0879 | 673.984 | 0 | -13.3146
7 | 5.5 | 4.468% | 125.1015 | 12.5% | 6:00 | 6:08 | -3.3515 | 0 | -109.8809 | 121.6485 | 0 | -94.2539 | 246.6485 | 0 | -78.627 | 346.6485 | 0 | -66.1254 | 496.6485 | 0 | -47.3731 | 596.6485 | 0 | -34.8715
8 | 10.7 | 8.692% | 243.3794 | 24.32% | 7:00 | 7:15 | -121.6294 | -3.3515 | -217.1198 | 3.3706 | 0 | -183.3668 | 128.3706 | 0 | -152.9652 | 228.3706 | 0 | -128.644 | 378.3706 | 0 | -92.1622 | 478.3706 | 0 | -67.841
9 | 9.3 | 7.555% | 211.5353 | 21.14% | 8:00 | 8:13 | -89.7853 | -124.9809 | -310.7795 | 35.2147 | 0 | -159.3748 | 160.2147 | 0 | -132.9511 | 260.2147 | 0 | -111.8121 | 410.2147 | 0 | -80.1036 | 510.2147 | 0 | -58.9646
10 | 7.5 | 6.093% | 170.593 | 17.05% | 9:00 | 9:10 | -48.843 | -214.7662 | -364.6038 | 76.157 | 0 | -128.5281 | 201.157 | 0 | -107.2186 | 301.157 | 0 | -90.171 | 451.157 | 0 | -64.5997 | 551.157 | 0 | -47.5521
11 | 6.7 | 5.443% | 152.3964 | 15.23% | 10:00 | 10:09 | -30.6464 | -263.6093 | -397.4642 | 94.3536 | 0 | -114.8184 | 219.3536 | 0 | -95.782 | 319.3536 | 0 | -80.5528 | 469.3536 | 0 | -57.709 | 569.3536 | 0 | -42.4799
12 | 5.9 | 4.793% | 134.1998 | 13.41% | 11:00 | 11:08 | -12.4498 | -294.2557 | -412.1279 | 112.5502 | 0 | -101.1088 | 237.5502 | 0 | -84.3453 | 337.5502 | 0 | -70.9346 | 487.5502 | 0 | -50.8184 | 587.5502 | 0 | -37.4076
13 | 5.2 | 4.224% | 118.2778 | 11.82% | 12:00 | 12:07 | 3.4722 | -306.7055 | -410.5929 | 128.4722 | 0 | -89.1128 | 253.4722 | 0 | -74.3382 | 353.4722 | 0 | -62.5186 | 503.4722 | 0 | -44.7891 | 603.4722 | 0 | -32.9694
14 | 4.4 | 3.574% | 100.0812 | 10% | 13:00 | 13:06 | 21.6688 | -303.2333 | -391.1381 | 146.6688 | 0 | -75.4032 | 271.6688 | 0 | -62.9016 | 371.6688 | 0 | -52.9003 | 521.6688 | 0 | -37.8985 | 621.6688 | 0 | -27.8972
15 | 3.8 | 3.087% | 86.4338 | 8.637% | 14:00 | 14:05 | 35.3162 | -281.5646 | -357.4823 | 160.3162 | 0 | -65.1209 | 285.3162 | 0 | -54.3241 | 385.3162 | 0 | -45.6867 | 535.3162 | 0 | -32.7305 | 635.3162 | 0 | -24.0931
16 | 3.9 | 3.168% | 88.7084 | 8.865% | 15:00 | 15:05 | 33.0416 | -246.2484 | -324.1639 | 158.0416 | 0 | -66.8346 | 283.0416 | 0 | -55.7537 | 383.0416 | 0 | -46.8889 | 533.0416 | 0 | -33.5918 | 633.0416 | 0 | -24.7271
17 | 4.5 | 3.656% | 102.3558 | 10.23% | 16:00 | 16:06 | 19.3942 | -213.2067 | -303.1093 | 144.3942 | 0 | -77.1169 | 269.3942 | 0 | -64.3312 | 369.3942 | 0 | -54.1026 | 519.3942 | 0 | -38.7598 | 619.3942 | 0 | -28.5312
18 | 6.5 | 5.28% | 147.8473 | 14.77% | 17:00 | 17:09 | -26.0973 | -193.8126 | -323.6718 | 98.9027 | 0 | -111.391 | 223.9027 | 0 | -92.9228 | 323.9027 | 0 | -78.1482 | 473.9027 | 0 | -55.9864 | 573.9027 | 0 | -41.2118
19 | 9.5 | 7.717% | 216.0845 | 21.59% | 18:00 | 18:13 | -94.3345 | -219.9098 | -409.7041 | 30.6655 | 0 | -162.8023 | 155.6655 | 0 | -135.8103 | 255.6655 | 0 | -114.2166 | 405.6655 | 0 | -81.8262 | 505.6655 | 0 | -60.2326
20 | 9 | 7.311% | 204.7116 | 20.46% | 19:00 | 19:12 | -82.9616 | -314.2443 | -494.0494 | 42.0384 | 0 | -154.2337 | 167.0384 | 0 | -128.6623 | 267.0384 | 0 | -108.2052 | 417.0384 | 0 | -77.5196 | 517.0384 | 0 | -57.0625
21 | 7.5 | 6.093% | 170.593 | 17.05% | 20:00 | 20:10 | -48.843 | -397.2059 | -547.0435 | 76.157 | 0 | -128.5281 | 201.157 | 0 | -107.2186 | 301.157 | 0 | -90.171 | 451.157 | 0 | -64.5997 | 551.157 | 0 | -47.5521
22 | 6 | 4.874% | 136.4744 | 13.64% | 21:00 | 21:08 | -14.7244 | -446.0489 | -565.919 | 110.2756 | 0 | -102.8225 | 235.2756 | 0 | -85.7749 | 335.2756 | 0 | -72.1368 | 485.2756 | 0 | -51.6797 | 585.2756 | 0 | -38.0417
23 | 4.5 | 3.656% | 102.3558 | 10.23% | 22:00 | 22:06 | 19.3942 | -460.7734 | -550.6759 | 144.3942 | 0 | -77.1169 | 269.3942 | 0 | -64.3312 | 369.3942 | 0 | -54.1026 | 519.3942 | 0 | -38.7598 | 619.3942 | 0 | -28.5312
24 | 3 | 2.437% | 68.2372 | 6.819% | 23:00 | 23:04 | 53.5128 | -441.3792 | -501.3142 | 178.5128 | 0 | -51.4112 | 303.5128 | 0 | -42.8874 | 403.5128 | 0 | -36.0684 | 553.5128 | 0 | -25.8399 | 653.5128 | 0 | -19.0208
1 | [7 empty] | -387.8664 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
2 | [7 empty] | -317.2943 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 | [7 empty] | -229.6629 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 | [7 empty] | -136.345 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 | [7 empty] | -37.3408 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
6 | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
7 | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
8 | [7 empty] | -3.3515 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Total | 123.1 | 100% | 2800 | [5 empty] | 1 |  |  | 1.1 |  |  | 1.2 |  |  | 1.3 |  |  | 1.4 |  |  | 1.5
DHW kW |  |  | 116.6667 | [5 empty] | 1150 | kW |  | 1275 |  |  | 1400 |  |  | 1500 |  |  | 1650 |  |  | 1750
Heating kW |  |  | 1028.25 | [5 empty] | 121.75 | kW |  | 246.75 |  |  | 371.75 |  |  | 471.75 |  |  | 621.75 |  |  | 721.75
Minimum Boiler Power |  |  | 1144.9167
[9 empty] | -565.919 | kWh |  | -183.3668 |  |  | -152.9652 |  |  | -128.644 |  |  | -92.1622 |  |  | -67.841
Selected Boiler Power | [8 empty] | 13859.241 | litres |  | 4490.6145 |  |  | 3746.0874 |  |  | 3150.4657 |  |  | 2257.0331 |  |  | 1661.4114
Spare for DHW
Min kWh
Central Buffer Volume
| Boiler Size | Buffer Size
| 1150 | 13859.241
| 1275 | 4490.6145
| 1400 | 3746.0874
| 1500 | 3150.4657
| 1650 | 2257.0331
| 1750 | 1661.4114
Note on E2: Calculted hourly volumes from EST Data weightings
Note on F2: With a known volume per hour, and a peak diversified flow, the maximum possible draw off is the hourly volume drawn in a single hit at full diversity.

## Pipes
Diameter | Wal | Bore | Material | Roughness Constant | Tube Thermal Conductivity | Insulation Thermal Conductivity | Insulation Thickness | Cost | ro | ri | rs | Thermal Loss
mm | mm | mm |  |  | W/mk | W/mK | mm | £/m |  |  |  | W/m/K
10 | 0.8 | 8.4 | Copper | 140 | 401 | 0.034 | 40 | 1.6784 | 0.005 | 0.0042 | 0.045 | 0.097226
12 | 0.8 | 10.4 | Copper | 140 | 401 | 0.034 | 40 | 2 | 0.006 | 0.0052 | 0.046 | 0.10488
15 | 1 | 13 | Copper | 140 | 401 | 0.034 | 40 | 2.0933 | 0.0075 | 0.0065 | 0.0475 | 0.11573
22 | 1 | 20 | Copper | 140 | 401 | 0.034 | 40 | 4.4867 | 0.011 | 0.01 | 0.051 | 0.13927
28 | 1 | 26 | Copper | 140 | 401 | 0.034 | 40 | 5.7133 | 0.014 | 0.013 | 0.054 | 0.15825
35 | 1.2 | 32.6 | Copper | 140 | 401 | 0.034 | 40 | 10.98 | 0.0175 | 0.0163 | 0.0575 | 0.17958
42 | 1.5 | 39 | Copper | 140 | 401 | 0.034 | 40 | 13.3933 | 0.021 | 0.0195 | 0.061 | 0.20033
54 | 1.5 | 51 | Copper | 140 | 401 | 0.034 | 40 | 17.4667 | 0.027 | 0.0255 | 0.067 | 0.23505
75 | 1.5 | 72 | Steel | 140 | 401 | 0.034 | 40 | 25 | 0.0375 | 0.036 | 0.0775 | 0.29428
100 | 1.5 | 97 | Steel | 140 | 401 | 0.034 | 40 | 33.3333 | 0.05 | 0.0485 | 0.09 | 0.36344
150 | 1.5 | 147 | Steel | 140 | 401 | 0.034 | 40 | 50 | 0.075 | 0.0735 | 0.115 | 0.49978
200 | 1.5 | 197 | Steel | 140 | 401 | 0.034 | 40 | 66.6667 | 0.1 | 0.0985 | 0.14 | 0.6349
250 | 1.5 | 247 | Steel | 140 | 401 | 0.034 | 40 | 83.3333 | 0.125 | 0.1235 | 0.165 | 0.76946
http://www.engineeringtoolbox.com/conductive-heat-loss-cylinder-pipe-d_1487.html
Q = (ti - to) / [(ln(ro / ri) / 2 π k L) + (ln(rs / ro) / 2 π ks L)]
http://www.insulationgiant.co.uk/Rockwool-Heating-and-Ventilation-Pipe-Insulation-40mm-Wall-Thickness/p/9000094465
Note on J2: Based on quoted prices for 100m lengths

## Energy Use
| Power |  | Hours/Year | Annual Energy
Losses in Buildings | 29.3272 | kW | 8760 | 256905.8709 | kWh
Losses in Netork | 9.7629 | kW | 8760 | 85523.0158 | kWh
Domestic Hot Water |  |  |  | 1022000 | kWh
Central Heating | 1080 | kW | 750 | 810000 | kWh

## Energy Generation
NOT IMPLEMENTED YET
Chart of Boiler Efficiency at different Flow Temperatures
Temperature | Peak | 30 | 40 | 50 | 60 | 70 | 80 | 90
Gas Boiler | 90 | 95% | 95% | 95% | 95% | 90% | 85% | 80%
CHP | 90 | 100% | 100% | 100% | 100% | 100% | 90% | 80%
Heat Pump | 55 | 500% | 400% | 300% | 200% | 0% | 0% | 0%
Solar Thermal | 90 | 100% | 100% | 95% | 95% | 90% | 85% | 80%
Biomass | 90 | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Peak Load Flow Temperature | 85 | C |  | 85%
Summer Flow Temperature | 65 | C
Return DHW | 25 | C
Return CH | 45 | C