Update Procedure for HIU Controller Version 1 (Dekimo)

This procedure describes the update of the firmware of the Dekimo HIU controller. The controller is shown below:

# Preparation

A laptop with the correct binary file “firmware.bin” is needed as well as an Mini USB cable.

The correct firmware file “firmware.bin” is needed accessible on the laptop , which will be used to execute the update.

A USB cable which connects the laptop with the controller is needed, where the controller side of the cable is a “Mini USB” connector and the other end of the cable fits the laptop USB socket. This picture shows a USB-A (left) to Mini USB (right) cable:

# Update Procedure

- Switch off the power to the controller

- Connect the running laptop with the USB cable to the controller

- Keep the recessed button pressed by using a wire or ball point pen WHILST switching on the power supply of the controller:

- The LED will light up in white and the controller will appear as an additional external drive on the laptop (CRP DISABLD)

- Let go of the recessed button

- Delete the old file “firmware.bin” from the drive “CRP DISABLD”

- Copy the file “firmware.bin” from the laptop to the external drive ”CRP DISABLD” which is the controller

- Power off the controller and disconnect the USB cable

- Repower the controller and test the HIU