## Notes
Heat Network Sizing Tool for 480 Properties
09/0.2017
This is a fully worked example for pipe sizing on a district heating network, feeding 480 properties split into 10 blocks of 48.
This and other examples can be downoaded from our wiki site at:
http://www.heatweb.co.uk/w/index.php?title=Pipework_Calculation_Examples
Thermal Integration Ltd.
0845 2411441
www.heatweb.com

## Summary
Heat Network Sizing Tool for 480 Properties
Dwelling Peak DHW | 45 | Kw |  | Peak DHW Load | 1000.6874 | kW | 3.4037 | l/s | Cost of Pipework | 57916.8
Dwelling Peak CH | 3 | Kw |  | Peak CH Load | 1080 | kW | 4.2857 | l/s
DP across load (HIU+meter) | 55 | kPa |  | Peak Load | 2028.9374 | kW | 7.4841 | l/s
Peak Load Flow Temperature | 90 | C
Summer Flow Temperature | 65 | C |  | Peak Load Heat Loss | 47.6856 | kW | 2.35%
Return DHW | 20 | C
Return CH | 30 | C |  | Peak Pressure Drop | 197.8336 | kPa
Occupants per property | 3 |  |  | Summer Peak Pressure Drop | 226.1155 | kPa
Flush Rate (HIU function) | 20 | l/m
Peak erosion velocity | 1 | m/s |  | Peak Pressure Drop, Building | 114.6971 | kPa
Fixed DHW/property/day | 35 | litres | info | Summer Peak Pressure Drop, Building | 176.7293 | kPa
DHW/person/day | 20 | litres
DHW Temp Rise (for above) | 40 | C |  | Peak Velocity | 1.1532 | m/s
Hours Central Heating per Year (peak/flat) | 600 | hours |  | Peak Erosion Velocity | 0.63041 | m/s | 1 | m/s max.
Insulation Thickness, Flow | 50 | mm |  | Minimum Velocity | 0.51724 | m/s | 0.5 | m/s min.
Insulation Thickness, Return | 30 | mm
Min Velocity Network (F/R) | 0.5 | 0.5 | m/s | DHW delay with cold laterals / hot riser | 23.9201 | seconds
Min Velocity Buildings (F/R) | 0.75 | 0.5 | m/s
Heating Season | 120 | days
HIU Standby Return Temperature | 25 | C | [8 empty] | Heat Pump / Gas Boiler Mix
HIU Standby Flow Rate | 0 | l/hour | [8 empty] | Peak Load Efficiency | 143.9% | 0.17784 | Kg CO2/kWh
Hot Water Priority | 1 | [9 empty] | Summer Efficiency | 260.5% | 0.15247 | Kg CO2/kWh
Thermal Integration Ltd.
0845 2411441
www.heatweb.com

## Pipe Sizing
| Example for index flat on 480 property scheme, with 10 risers, feeding 4 storey buildings | [40 empty] | Columns W,X,Y for Herz Williams Pressure Loss Calculation
[7 empty] | Physical |  |  |  |  | Loading | [22 empty] | Pipe Selection |  |  |  | Pressure Loss | [8 empty] | Volume |  | Velocity |  |  |  |  | Thermal Losses | [18 empty] | Summer Velocity Figures
ID | Description | Class | Properties | Min | Occupants | Daily | Length | Elbow | Elbow | Tee | Tee | Count | Total | Danish | DHW | DHW | Min | Est | Htg | Htg | DHW | Htg | DHW | Peak % | Htg | Htg | Htg % | Htg % | Peak Trickle Flow | Summer Trickle Flow | Total | Total | Pipe Area | Pipe Bore | Pipe Bore | Pipe Size | Material | Roughness | f = friction (mm H20 per 100 m pipe) | f = friction (kPa per 100 m pipe) | Head loss (mm H20) | kPa | Pa/m | Equiv | kPa | kPa | kPa | Area | Volume | Peak | Continuous | Weighed | Flush | Accumulative | Thermal | Ambient Temperature | Peak Load Pipe Temp | Summer Peak Load Pipe Temp | Standby | Peak | Summer Peak Losses | Standby | Decay Time to 50C | Standby Losses | Peak | Summer Peak Losses | % Time Standby Temp | % Time Peak Temp | % Time Summer Peak Temp | Average Losses | Average | Losses per metre | % Share | DHW | f = friction (mm H20 per 100 m pipe) | f = friction (kPa per 100 m pipe) | Head loss (mm H20) | kPa | Pa/m | kPa | kPa | Peak | Continuous | Weighed | Tube | Tube
|  |  |  | Target |  | DHW | m | 90° | 45° | Line | Branch |  | Length | DHW | Diversity | kW | HIUs | Taps | Diversity | kw | Priority | kw | litre/s | time at | litre/s | litre/s | of Peak | of Daily |  | litres/s | Peak | Peak | mm2 | Calculated | Selected | [6 empty] | pipes |  | Length | fittings | TOTAL | Share |  | litres | Velocity | Velocity | Erosion | time | Flush time | Rating |  |  |  | Temp | Losses |  | Losses |  |  | Losses | [5 empty] | Losses |  | Losses | litres/s |  |  |  | pipes |  | fittings | TOTAL | Velocity | Velocity | Erosion | Cost | Cost
|  |  |  | Velocity |  | kWh | [7 empty] | DS439 |  |  | Running | Running |  |  | Saving | NET |  | Peak | peak | minus | Flow | kWh |  |  | kW | litre/s |  |  | mm | mm | [7 empty] | fittings | [5 empty] | m/s | m/s | Velocity | seconds | seconds | W/m/K | C |  |  | C | kW | kW | kW | hours |  | kW | kW |  |  |  | kW | kW | W/m |  | Summer | [7 empty] | m/s | m/s | Velocity | £/m | £
|  |  |  | m/s | [9 empty] | kW | [6 empty] | kW |  |  |  |  | priority | [25 empty] | m/s |  |  |  |  | C | C | [5 empty] | TOTAL | TOTAL | TOTAL |  |  |  |  | TOTAL | [12 empty] | m/s
2232.5246
1F | Run to 1st riser | Flow | 480 | 0.5 | 1440 | 2128 | 100 | 4 |  | 1 |  | 1 | 100 | 1000.6874 | 0.046328 | 1000.6874 | 23 | 83.3906 | 0.75 | 1080 | 51.75 | 1028.25 | 3.4037 | 8.861% | 4.2857 | 4.0804 | 54.52% | 92.06% | 0 | 0 | 2028.9374 | 7.4841 | 14968.1113 | 138.0507 | 97 | 100 | Steel | 140 | 1142.8551 | 11.2114 | 1142.8551 | 11.2114 | 112.1141 | 13.58 | 1.5225 | 12.7339 | 6.437% | 7389.8051 | 738.9805 | 1.0128 | 0.57995 | 0.63041 | 2216.9415 | 6697.5739 | 0.3082 | 12 | 90 | 65 | 65 | 2.404 | 1.6335 | 1.6335 | 14.3454 | 1.6335 | 2.404 | 1.6335 | 0% | 32.88% | 67.12% | 1.8868 | 1.8868 | 18.8677 | 6.54% | 5.2946 | 602.0532 | 5.9061 | 602.0532 | 5.9061 | 59.0614 | 0.80205 | 6.7082 | 0.46059 | 0 | 0.1371 | 33.3333 | 3333.3333
2F | Run to 2nd Riser | Flow | 432 | 0.5 | 1296 | 1915.2 | 30 |  | 2 | 1 |  | 1 | 30 | 922.4307 | 0.04745 | 922.4307 | 21 | 76.8692 | 0.8 | 1036.8 | 50.4 | 986.4 | 3.1375 | 8.651% | 4.1143 | 3.9143 | 55.51% | 92.52% | 0 | 0 | 1908.8307 | 7.0518 | 14103.6099 | 134.0048 | 97 | 100 | Steel | 140 | 1023.6266 | 10.0418 | 307.088 | 3.0125 | 100.4178 | 5.044 | 0.50651 | 3.519 | 1.779% | 7389.8051 | 221.6942 | 0.95426 | 0.55675 | 0.60161 | 665.0825 | 4480.6324 | 0.3082 | 12 | 90 | 65 | 65 | 0.72119 | 0.49004 | 0.49004 | 14.3454 | 0.49004 | 0.72119 | 0.49004 | 0% | 32.88% | 67.12% | 0.56603 | 0.56603 | 18.8677 | 1.962% | 4.8806 | 517.7731 | 5.0794 | 155.3319 | 1.5238 | 50.7935 | 0.2562 | 1.78 | 0.42457 | 0 | 0.12488 | 33.3333 | 1000
3F | Run to 3rd Riser | Flow | 384 | 0.5 | 1152 | 1702.4 | 30 |  | 2 | 1 |  | 1 | 30 | 842.9633 | 0.048783 | 842.9633 | 19 | 70.2469 | 0.8 | 921.6 | 45.6 | 876 | 2.8672 | 8.415% | 3.6571 | 3.4762 | 54.8% | 92.51% | 0 | 0 | 1718.9633 | 6.3434 | 12686.8249 | 127.096 | 97 | 100 | Steel | 140 | 841.3788 | 8.2539 | 252.4136 | 2.4762 | 82.5393 | 5.044 | 0.41633 | 2.8925 | 1.462% | 7389.8051 | 221.6942 | 0.8584 | 0.49489 | 0.53508 | 665.0825 | 3815.5499 | 0.3082 | 12 | 90 | 65 | 65 | 0.72119 | 0.49004 | 0.49004 | 14.3454 | 0.49004 | 0.72119 | 0.49004 | 0% | 32.88% | 67.12% | 0.56603 | 0.56603 | 18.8677 | 1.962% | 4.4601 | 438.2075 | 4.2988 | 131.4622 | 1.2896 | 42.9882 | 0.21683 | 1.5065 | 0.388 | 0 | 0.11255 | 33.3333 | 1000
4F | Run to 4th Riser | Flow | 336 | 0.5 | 1008 | 1489.6 | 30 |  | 2 | 1 |  | 1 | 30 | 762.0497 | 0.0504 | 762.0497 | 17 | 63.5041 | 0.8 | 806.4 | 40.8 | 765.6 | 2.592 | 8.145% | 3.2 | 3.0381 | 53.96% | 92.5% | 0 | 0 | 1527.6497 | 5.6301 | 11260.202 | 119.737 | 97 | 100 | Steel | 140 | 674.5986 | 6.6178 | 202.3796 | 1.9853 | 66.1781 | 5.044 | 0.3338 | 2.3191 | 1.172% | 7389.8051 | 221.6942 | 0.76187 | 0.43303 | 0.46853 | 665.0825 | 3150.4674 | 0.3082 | 12 | 90 | 65 | 65 | 0.72119 | 0.49004 | 0.49004 | 14.3454 | 0.49004 | 0.72119 | 0.49004 | 0% | 32.88% | 67.12% | 0.56603 | 0.56603 | 18.8677 | 1.962% | 4.032 | 363.5091 | 3.566 | 109.0527 | 1.0698 | 35.6602 | 0.17987 | 1.2497 | 0.35075 | 0 | 0.1001 | 33.3333 | 1000
5F | Run to 5th Riser | Flow | 288 | 0.5 | 864 | 1276.8 | 30 |  | 2 | 1 |  | 1 | 30 | 679.3666 | 0.05242 | 679.3666 | 16 | 56.6139 | 0.85 | 734.4 | 40.8 | 693.6 | 2.3108 | 7.831% | 2.9143 | 2.7524 | 54.36% | 92.88% | 0 | 0 | 1372.9666 | 5.0632 | 10126.3033 | 113.5483 | 97 | 100 | Steel | 140 | 554.2134 | 5.4368 | 166.264 | 1.631 | 54.3683 | 5.044 | 0.27423 | 1.9053 | 0.9631% | 7389.8051 | 221.6942 | 0.68515 | 0.39437 | 0.42439 | 665.0825 | 2485.385 | 0.3082 | 12 | 90 | 65 | 65 | 0.72119 | 0.49004 | 0.49004 | 14.3454 | 0.49004 | 0.72119 | 0.49004 | 0% | 32.88% | 67.12% | 0.56603 | 0.56603 | 18.8677 | 1.962% | 3.5945 | 293.8591 | 2.8828 | 88.1577 | 0.86483 | 28.8276 | 0.14541 | 1.0102 | 0.3127 | 0 | 0.087504 | 33.3333 | 1000
6F | Run to 6th Riser | Flow | 240 | 0.5 | 720 | 1064 | 30 |  | 2 | 1 |  | 1 | 30 | 594.4483 | 0.055042 | 594.4483 | 14 | 49.5374 | 0.85 | 612 | 35.7 | 576.3 | 2.0219 | 7.458% | 2.4286 | 2.2869 | 53.07% | 92.86% | 0 | 0 | 1170.7483 | 4.3088 | 8617.6758 | 104.7491 | 97 | 100 | Steel | 140 | 411.0782 | 4.0327 | 123.3235 | 1.2098 | 40.3268 | 5.044 | 0.20341 | 1.4132 | 0.7143% | 7389.8051 | 221.6942 | 0.58308 | 0.32864 | 0.35398 | 665.0825 | 1820.3025 | 0.3082 | 12 | 90 | 65 | 65 | 0.72119 | 0.49004 | 0.49004 | 14.3454 | 0.49004 | 0.72119 | 0.49004 | 0% | 32.88% | 67.12% | 0.56603 | 0.56603 | 18.8677 | 1.962% | 3.1452 | 229.4783 | 2.2512 | 68.8435 | 0.67535 | 22.5118 | 0.11355 | 0.7889 | 0.27361 | 0 | 0.074721 | 33.3333 | 1000
7F | Run to 7th Riser | Flow | 192 | 0.5 | 576 | 851.2 | 30 |  | 2 | 1 |  | 1 | 30 | 506.5804 | 0.058632 | 506.5804 | 12 | 42.215 | 0.85 | 489.6 | 30.6 | 459 | 1.7231 | 7.001% | 1.9429 | 1.8214 | 51.39% | 92.83% | 0 | 0 | 965.5804 | 3.5445 | 7088.9826 | 95.0052 | 72 | 75 | Steel | 140 | 1220.8151 | 11.9762 | 366.2445 | 3.5929 | 119.762 | 3.744 | 0.44839 | 4.0412 | 2.043% | 4071.5006 | 122.145 | 0.87056 | 0.47718 | 0.51461 | 366.4351 | 1155.2201 | 0.25213 | 12 | 90 | 65 | 65 | 0.58998 | 0.40088 | 0.40088 | 9.6615 | 0.40088 | 0.58998 | 0.40088 | 0% | 32.88% | 67.12% | 0.46305 | 0.46305 | 15.435 | 1.605% | 2.6803 | 727.5748 | 7.1375 | 218.2724 | 2.1413 | 71.3751 | 0.26723 | 2.4085 | 0.4232 | 0 | 0.11198 | 25 | 750
8F | Run to 8th Riser | Flow | 144 | 0.5 | 432 | 638.4 | 30 |  | 2 | 1 |  | 1 | 30 | 414.56 | 0.063975 | 414.56 | 10 | 34.5467 | 0.9 | 388.8 | 27 | 361.8 | 1.4101 | 6.416% | 1.5429 | 1.4357 | 50.45% | 93.15% | 0 | 0 | 776.36 | 2.8458 | 5691.5646 | 85.1277 | 72 | 75 | Steel | 140 | 812.9382 | 7.9749 | 243.8815 | 2.3925 | 79.7492 | 3.744 | 0.29858 | 2.6911 | 1.36% | 4071.5006 | 122.145 | 0.69895 | 0.37894 | 0.4071 | 366.4351 | 788.785 | 0.25213 | 12 | 90 | 65 | 65 | 0.58998 | 0.40088 | 0.40088 | 9.6615 | 0.40088 | 0.58998 | 0.40088 | 0% | 32.88% | 67.12% | 0.46305 | 0.46305 | 15.435 | 1.605% | 2.1934 | 501.9271 | 4.9239 | 150.5781 | 1.4772 | 49.239 | 0.18435 | 1.6615 | 0.34633 | 0 | 0.087727 | 25 | 750
9F | Run to 9th Riser | Flow | 96 | 0.5 | 288 | 425.6 | 30 |  | 2 | 1 |  | 1 | 30 | 316.0416 | 0.073158 | 316.0416 | 8 | 26.3368 | 0.9 | 259.2 | 21.6 | 237.6 | 1.075 | 5.611% | 1.0286 | 0.94286 | 46.73% | 93.05% | 0 | 0 | 553.6416 | 2.0178 | 4035.6573 | 71.6824 | 51 | 54 | Copper | 140 | 2302.4506 | 22.587 | 690.7352 | 6.7761 | 225.8704 | 2.652 | 0.59901 | 7.3751 | 3.728% | 2042.8189 | 61.2846 | 0.98777 | 0.50351 | 0.54225 | 183.8537 | 422.35 | 0.20385 | 12 | 90 | 65 | 65 | 0.47701 | 0.32412 | 0.32412 | 5.9956 | 0.32412 | 0.47701 | 0.32412 | 0% | 32.88% | 67.12% | 0.37438 | 0.37438 | 12.4795 | 1.298% | 1.6722 | 1625.7875 | 15.949 | 487.7363 | 4.7847 | 159.4898 | 0.42297 | 5.2077 | 0.52622 | 0 | 0.12465 | 17.4667 | 524
10F | Run to 10th riser (ground floor) | Flow | 48 | 0.5 | 144 | 212.8 | 30 | 1 | 2 |  |  | 1 | 30 | 204.9702 | 0.094894 | 204.9702 | 5 | 17.0809 | 0.9 | 129.6 | 13.5 | 116.1 | 0.69718 | 4.326% | 0.51429 | 0.46071 | 39.79% | 92.9% | 0 | 0 | 321.0702 | 1.1579 | 2315.7838 | 54.3006 | 51 | 54 | Copper | 140 | 823.1098 | 8.0747 | 246.933 | 2.4224 | 80.7471 | 3.162 | 0.25532 | 2.6777 | 1.354% | 2042.8189 | 61.2846 | 0.56681 | 0.25175 | 0.27301 | 183.8537 | 238.4963 | 0.20385 | 25 | 90 | 65 | 65 | 0.39751 | 0.24462 | 0.24462 | 7.1947 | 0.24462 | 0.39751 | 0.24462 | 0% | 32.88% | 67.12% | 0.29488 | 0.29488 | 9.8294 | 1.022% | 1.0845 | 729.1026 | 7.1525 | 218.7308 | 2.1457 | 71.525 | 0.22616 | 2.3719 | 0.34128 | 0 | 0.070982 | 17.4667 | 524
11F | Riser to 1st floor | Flow | 36 | 0.75 | 108 | 159.6 | 4 |  |  | 1 |  | 10 | 40 | 173.24 | 0.10694 | 173.24 | 4 | 14.4367 | 0.95 | 102.6 | 11.4 | 91.2 | 0.58925 | 3.839% | 0.40714 | 0.3619 | 38.05% | 93.2% | 0 | 0 | 264.44 | 0.95116 | 1268.2086 | 40.1838 | 39 | 42 | Copper | 140 | 2109.2357 | 20.6916 | 84.3694 | 0.82766 | 206.916 | 0.78 | 0.16139 | 0.98906 | 0.4999% | 1194.5896 | 4.7784 | 0.79622 | 0.34082 | 0.36883 | 14.3351 | 54.6426 | 0.17537 | 25 | 90 | 65 | 65 | 0.045596 | 0.028059 | 0.028059 | 4.8906 | 0.28059 | 0.45596 | 0.28059 | 1% | 32.55% | 66.45% | 0.033767 | 0.33767 | 8.4417 | 1.17% | 0.91661 | 1969.5709 | 19.3215 | 78.7828 | 0.77286 | 193.2149 | 0.15071 | 0.92357 | 0.49327 | 0 | 0.096643 | 13.3933 | 535.7333
12F | Riser to 2nd floor | Flow | 24 | 0.75 | 72 | 106.4 | 4 |  |  | 1 |  | 10 | 40 | 138.2608 | 0.12802 | 138.2608 | 4 | 11.5217 | 0.95 | 68.4 | 11.4 | 57 | 0.47027 | 3.207% | 0.27143 | 0.22619 | 32.48% | 92.78% | 0 | 0 | 195.2608 | 0.69647 | 928.6205 | 34.3854 | 32.6 | 35 | Copper | 140 | 2832.807 | 27.7898 | 113.3123 | 1.1116 | 277.8984 | 0.652 | 0.18119 | 1.2928 | 0.6535% | 834.689 | 3.3388 | 0.8344 | 0.32519 | 0.3531 | 10.0163 | 40.3075 | 0.15825 | 25 | 90 | 65 | 65 | 0.041145 | 0.02532 | 0.02532 | 3.7868 | 0.2532 | 0.41145 | 0.2532 | 2% | 32.22% | 65.78% | 0.030419 | 0.30419 | 7.6047 | 1.054% | 0.73154 | 3102.6628 | 30.4371 | 124.1065 | 1.2175 | 304.3712 | 0.19845 | 1.4159 | 0.56341 | 0 | 0.10089 | 10.98 | 439.2
13F | Riser to 3rd floor | Flow | 12 | 0.75 | 36 | 53.2 | 4 |  |  |  | 1 | 10 | 40 | 97.0051 | 0.17964 | 97.0051 | 3 | 8.0838 | 0.95 | 34.2 | 8.55 | 25.65 | 0.32995 | 2.285% | 0.13571 | 0.10179 | 23.58% | 92.05% | 0 | 0 | 122.6551 | 0.43174 | 575.6468 | 27.0728 | 26 | 28 | Copper | 140 | 3512.3435 | 34.4561 | 140.4937 | 1.3782 | 344.5609 | 1.56 | 0.53751 | 1.9158 | 0.9684% | 530.9287 | 2.1237 | 0.81317 | 0.25562 | 0.28099 | 6.3711 | 30.2912 | 0.14056 | 25 | 90 | 65 | 65 | 0.036546 | 0.02249 | 0.02249 | 2.7119 | 0.2249 | 0.36546 | 0.2249 | 3% | 31.89% | 65.11% | 0.026972 | 0.26972 | 6.743 | 0.935% | 0.51325 | 4838.5012 | 47.4657 | 193.54 | 1.8986 | 474.657 | 0.74046 | 2.6391 | 0.62146 | 0 | 0.093943 | 5.7133 | 228.5333
14F | Lateral | Periphery | 6 | 0.75 | 18 | 26.6 | 10 |  |  | 1 |  | 80 | 800 | 70.7904 | 0.35 | 94.5 | 3 | 7.875 | 1 | 18 | 9 | 9 | 0.32143 | 1.173% | 0.071429 | 0.035714 | 10% | 89.04% | 0 | 0 | 103.5 | 0.35714 | 476.1905 | 24.6233 | 20 | 22 | Copper | 140 | 8859.9077 | 86.9157 | 885.9908 | 8.6916 | 869.1569 | 0.4 | 0.34766 | 9.0392 | 4.569% | 314.159 | 3.1416 | 1.1368 | 0.22736 | 0.25738 | 9.4248 | 23.9201 | 0.12471 | 25 | 90 | 65 | 30 | 0.081062 | 0.049884 | 0.0062355 | 1.8086 | 0.49884 | 6.485 | 3.9907 | 10% | 29.59% | 60.41% | 0.054745 | 4.3796 | 5.4745 | 15.18% | 0.5 | 16521.8364 | 162.0792 | 1652.1836 | 16.2079 | 1620.7922 | 0.64832 | 16.8562 | 1.0231 | 0 | 0.1108 | 4.4867 | 3589.3333
15F | Lateral | Periphery | 4 | 0.75 | 12 | 17.7333 | 6 |  |  | 1 |  | 80 | 480 | 59.96 | 0.5 | 90 | 2 | 7.5 | 1 | 12 | 6 | 6 | 0.30612 | 0.821% | 0.047619 | 0.02381 | 7.216% | 89.04% | 0 | 0 | 96 | 0.32993 | 439.9093 | 23.6667 | 20 | 22 | Copper | 140 | 7650.4656 | 75.0511 | 459.0279 | 4.5031 | 750.5107 | 0.4 | 0.3002 | 4.8033 | 2.428% | 314.159 | 1.885 | 1.0502 | 0.15158 | 0.17844 | 5.6549 | 14.4953 | 0.12471 | 25 | 90 | 65 | 30 | 0.048637 | 0.029931 | 0.0037413 | 1.8086 | 0.29931 | 3.891 | 2.3944 | 15% | 27.95% | 57.05% | 0.03123 | 2.4984 | 5.205 | 8.66% | 0.47619 | 15094.3959 | 148.076 | 905.6638 | 8.8846 | 1480.7602 | 0.5923 | 9.4769 | 0.97442 | 0 | 0.088291 | 4.4867 | 2153.6
16F | Lateral | Periphery | 2 | 0.75 | 6 | 8.8667 | 6 |  |  |  | 1 | 80 | 480 | 46.5672 | 0.8 | 72 | 2 | 6 | 1 | 6 | 6 | 0 | 0.2449 | 0.5131% | 0.02381 | 0 | 0% | 0% | 0 | 0 | 72 | 0.2449 | 326.5306 | 20.39 | 20 | 22 | Copper | 140 | 4405.2078 | 43.2151 | 264.3125 | 2.5929 | 432.1509 | 1.2 | 0.51858 | 3.1115 | 1.573% | 314.159 | 1.885 | 0.77954 | 0.075788 | 0.093981 | 5.6549 | 8.8404 | 0.12471 | 25 | 90 | 65 | 30 | 0.048637 | 0.029931 | 0.0037413 | 1.8086 | 0.29931 | 3.891 | 2.3944 | 20% | 26.3% | 53.7% | 0.029613 | 2.369 | 4.9355 | 8.212% | 0.38095 | 9984.7775 | 97.9507 | 599.0867 | 5.877 | 979.5067 | 1.1754 | 7.0524 | 0.77954 | 0 | 0.05584 | 4.4867 | 2153.6
18F | Feed | Periphery | 1 | 0.75 | 3 | 4.4333 | 8 | 5 |  |  |  | 480 | 3840 | 37.59 | 1 | 45 | 1 | 3.75 | 1 | 3 | 3 | 0 | 0.15306 | 0.4105% | 0.011905 | 0 | 0% | 0% | 0 | 0 | 45 | 0.15306 | 204.0816 | 16.1197 | 13 | 15 | Copper | 140 | 15003.9723 | 147.189 | 1200.3178 | 11.7751 | 1471.8897 | 1.95 | 2.8702 | 14.6453 | 7.403% | 132.7322 | 1.0619 | 1.1532 | 0.08969 | 0.11606 | 3.1856 | 3.1856 | 0.10488 | 25 | 90 | 65 | 30 | 0.054537 | 0.033561 | 0.0041952 | 0.90861 | 2.0137 | 26.1779 | 16.1095 | 30% | 23.01% | 46.99% | 0.029579 | 14.1978 | 3.6974 | 49.22% | 0.2381 | 34007.7773 | 333.6163 | 2720.6222 | 26.6893 | 3336.163 | 6.5055 | 33.1948 | 1.1532 | 0 | 0.073883 | 2.0933 | 8038.4
HIU | Load | Load | 1 |  | 3 | 4.4333 | [5 empty] | 480 |  | 37.59 | 1 | 45 | 1 | 3.75 | 1 | 3 | 3 | 0 | 0.15306 | 0.4105% | 0.011905 | 0 | 0% | 0% | 0 | 0 | 45 | 0.15306 | [13 empty] | 55 | 27.8% | [9 empty] | 20 | [16 empty] | 0.2381 |  |  | 0 |  |  |  | 55
1F | Run to 1st riser | Return | 480 | 0.5 | 1440 | 2128 | 100 | 4 | 0 | 1 | 0 | 1 | 100 | 1000.6874 | 0.046328 | 1000.6874 | 23 | 83.3906 | 0.75 | 1080 | 51.75 | 1028.25 | 3.4037 | 8.861% | 4.2857 | 4.0804 | 54.52% | 92.06% | 0 | 0 | 2028.9374 | 7.4841 | 14968.1113 | 138.0507 | 97 | 100 | Steel | 140 | 1142.8551 | 11.2114 | 1142.8551 | 11.2114 | 112.1141 | 13.58 | 1.5225 | 12.7339 | 6.437% | 7389.8051 | 738.9805 | 1.0128 | 0.57995 | 0.63041 |  |  | 0.45452 | 12 | 25.4521 | 20 | 25 | 0.61143 | 0.36362 | 0.59088 |  | 0.59088 | 0.61143 | 0.36362 | 0% | 32.88% | 67.12% | 0.44509 | 0.44509 | 4.4509 | 1.543% | 5.2946 | 602.0532 | 5.9061 | 602.0532 | 5.9061 | 59.0614 | 0.80205 | 6.7082 | 0.46059 | 0 | 0.1371 | 33.3333 | 3333.3333
2F | Run to 2nd Riser | Return | 432 | 0.5 | 1296 | 1915.2 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 922.4307 | 0.04745 | 922.4307 | 21 | 76.8692 | 0.8 | 1036.8 | 50.4 | 986.4 | 3.1375 | 8.651% | 4.1143 | 3.9143 | 55.51% | 92.52% | 0 | 0 | 1908.8307 | 7.0518 | 14103.6099 | 134.0048 | 97 | 100 | Steel | 140 | 1023.6266 | 10.0418 | 307.088 | 3.0125 | 100.4178 | 5.044 | 0.50651 | 3.519 | 1.779% | 7389.8051 | 221.6942 | 0.95426 | 0.55675 | 0.60161 |  |  | 0.45452 | 12 | 25.5508 | 20 | 25 | 0.18477 | 0.10909 | 0.17726 |  | 0.17726 | 0.18477 | 0.10909 | 0% | 32.88% | 67.12% | 0.13397 | 0.13397 | 4.4656 | 0.4644% | 4.8806 | 517.7731 | 5.0794 | 155.3319 | 1.5238 | 50.7935 | 0.2562 | 1.78 | 0.42457 | 0 | 0.12488 | 33.3333 | 1000
3F | Run to 3rd Riser | Return | 384 | 0.5 | 1152 | 1702.4 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 842.9633 | 0.048783 | 842.9633 | 19 | 70.2469 | 0.8 | 921.6 | 45.6 | 876 | 2.8672 | 8.415% | 3.6571 | 3.4762 | 54.8% | 92.51% | 0 | 0 | 1718.9633 | 6.3434 | 12686.8249 | 127.096 | 97 | 100 | Steel | 140 | 841.3788 | 8.2539 | 252.4136 | 2.4762 | 82.5393 | 5.044 | 0.41633 | 2.8925 | 1.462% | 7389.8051 | 221.6942 | 0.8584 | 0.49489 | 0.53508 |  |  | 0.45452 | 12 | 25.48 | 20 | 25 | 0.18381 | 0.10909 | 0.17726 |  | 0.17726 | 0.18381 | 0.10909 | 0% | 32.88% | 67.12% | 0.13365 | 0.13365 | 4.4551 | 0.4633% | 4.4601 | 438.2075 | 4.2988 | 131.4622 | 1.2896 | 42.9882 | 0.21683 | 1.5065 | 0.388 | 0 | 0.11255 | 33.3333 | 1000
4F | Run to 4th Riser | Return | 336 | 0.5 | 1008 | 1489.6 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 762.0497 | 0.0504 | 762.0497 | 17 | 63.5041 | 0.8 | 806.4 | 40.8 | 765.6 | 2.592 | 8.145% | 3.2 | 3.0381 | 53.96% | 92.5% | 0 | 0 | 1527.6497 | 5.6301 | 11260.202 | 119.737 | 97 | 100 | Steel | 140 | 674.5986 | 6.6178 | 202.3796 | 1.9853 | 66.1781 | 5.044 | 0.3338 | 2.3191 | 1.172% | 7389.8051 | 221.6942 | 0.76187 | 0.43303 | 0.46853 |  |  | 0.45452 | 12 | 25.3962 | 20 | 25 | 0.18267 | 0.10909 | 0.17726 |  | 0.17726 | 0.18267 | 0.10909 | 0% | 32.88% | 67.12% | 0.13328 | 0.13328 | 4.4425 | 0.462% | 4.032 | 363.5091 | 3.566 | 109.0527 | 1.0698 | 35.6602 | 0.17987 | 1.2497 | 0.35075 | 0 | 0.1001 | 33.3333 | 1000
5F | Run to 5th Riser | Return | 288 | 0.5 | 864 | 1276.8 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 679.3666 | 0.05242 | 679.3666 | 16 | 56.6139 | 0.85 | 734.4 | 40.8 | 693.6 | 2.3108 | 7.831% | 2.9143 | 2.7524 | 54.36% | 92.88% | 0 | 0 | 1372.9666 | 5.0632 | 10126.3033 | 113.5483 | 97 | 100 | Steel | 140 | 554.2134 | 5.4368 | 166.264 | 1.631 | 54.3683 | 5.044 | 0.27423 | 1.9053 | 0.9631% | 7389.8051 | 221.6942 | 0.68515 | 0.39437 | 0.42439 |  |  | 0.45452 | 12 | 25.4361 | 20 | 25 | 0.18321 | 0.10909 | 0.17726 |  | 0.17726 | 0.18321 | 0.10909 | 0% | 32.88% | 67.12% | 0.13346 | 0.13346 | 4.4485 | 0.4626% | 3.5945 | 293.8591 | 2.8828 | 88.1577 | 0.86483 | 28.8276 | 0.14541 | 1.0102 | 0.3127 | 0 | 0.087504 | 33.3333 | 1000
6F | Run to 6th Riser | Return | 240 | 0.5 | 720 | 1064 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 594.4483 | 0.055042 | 594.4483 | 14 | 49.5374 | 0.85 | 612 | 35.7 | 576.3 | 2.0219 | 7.458% | 2.4286 | 2.2869 | 53.07% | 92.86% | 0 | 0 | 1170.7483 | 4.3088 | 8617.6758 | 104.7491 | 97 | 100 | Steel | 140 | 411.0782 | 4.0327 | 123.3235 | 1.2098 | 40.3268 | 5.044 | 0.20341 | 1.4132 | 0.7143% | 7389.8051 | 221.6942 | 0.58308 | 0.32864 | 0.35398 |  |  | 0.45452 | 12 | 25.3075 | 20 | 25 | 0.18146 | 0.10909 | 0.17726 |  | 0.17726 | 0.18146 | 0.10909 | 0% | 32.88% | 67.12% | 0.13288 | 0.13288 | 4.4293 | 0.4606% | 3.1452 | 229.4783 | 2.2512 | 68.8435 | 0.67535 | 22.5118 | 0.11355 | 0.7889 | 0.27361 | 0 | 0.074721 | 33.3333 | 1000
7F | Run to 7th Riser | Return | 192 | 0.5 | 576 | 851.2 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 506.5804 | 0.058632 | 506.5804 | 12 | 42.215 | 0.85 | 489.6 | 30.6 | 459 | 1.7231 | 7.001% | 1.9429 | 1.8214 | 51.39% | 92.83% | 0 | 0 | 965.5804 | 3.5445 | 7088.9826 | 95.0052 | 72 | 75 | Steel | 140 | 1220.8151 | 11.9762 | 366.2445 | 3.5929 | 119.762 | 3.744 | 0.44839 | 4.0412 | 2.043% | 4071.5006 | 122.145 | 0.87056 | 0.47718 | 0.51461 |  |  | 0.36344 | 12 | 25.1388 | 20 | 25 | 0.14326 | 0.087226 | 0.14174 |  | 0.14174 | 0.14326 | 0.087226 | 0% | 32.88% | 67.12% | 0.10565 | 0.10565 | 3.5216 | 0.3662% | 2.6803 | 727.5748 | 7.1375 | 218.2724 | 2.1413 | 71.3751 | 0.26723 | 2.4085 | 0.4232 | 0 | 0.11198 | 25 | 750
8F | Run to 8th Riser | Return | 144 | 0.5 | 432 | 638.4 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 414.56 | 0.063975 | 414.56 | 10 | 34.5467 | 0.9 | 388.8 | 27 | 361.8 | 1.4101 | 6.416% | 1.5429 | 1.4357 | 50.45% | 93.15% | 0 | 0 | 776.36 | 2.8458 | 5691.5646 | 85.1277 | 72 | 75 | Steel | 140 | 812.9382 | 7.9749 | 243.8815 | 2.3925 | 79.7492 | 3.744 | 0.29858 | 2.6911 | 1.36% | 4071.5006 | 122.145 | 0.69895 | 0.37894 | 0.4071 |  |  | 0.36344 | 12 | 25.0451 | 20 | 25 | 0.14223 | 0.087226 | 0.14174 |  | 0.14174 | 0.14223 | 0.087226 | 0% | 32.88% | 67.12% | 0.10531 | 0.10531 | 3.5104 | 0.365% | 2.1934 | 501.9271 | 4.9239 | 150.5781 | 1.4772 | 49.239 | 0.18435 | 1.6615 | 0.34633 | 0 | 0.087727 | 25 | 750
9F | Run to 9th Riser | Return | 96 | 0.5 | 288 | 425.6 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 316.0416 | 0.073158 | 316.0416 | 8 | 26.3368 | 0.9 | 259.2 | 21.6 | 237.6 | 1.075 | 5.611% | 1.0286 | 0.94286 | 46.73% | 93.05% | 0 | 0 | 553.6416 | 2.0178 | 4035.6573 | 71.6824 | 51 | 54 | Copper | 140 | 2302.4506 | 22.587 | 690.7352 | 6.7761 | 225.8704 | 2.652 | 0.59901 | 7.3751 | 3.728% | 2042.8189 | 61.2846 | 0.98777 | 0.50351 | 0.54225 |  |  | 0.2859 | 12 | 24.6726 | 20 | 25 | 0.10869 | 0.068615 | 0.1115 |  | 0.1115 | 0.10869 | 0.068615 | 0% | 32.88% | 67.12% | 0.081791 | 0.081791 | 2.7264 | 0.2835% | 1.6722 | 1625.7875 | 15.949 | 487.7363 | 4.7847 | 159.4898 | 0.42297 | 5.2077 | 0.52622 | 0 | 0.12465 | 17.4667 | 524
10F | Run to 10th riser (ground floor) | Return | 48 | 0.5 | 144 | 212.8 | 30 | 1 | 2 | 0 | 0 | 1 | 30 | 204.9702 | 0.094894 | 204.9702 | 5 | 17.0809 | 0.9 | 129.6 | 13.5 | 116.1 | 0.69718 | 4.326% | 0.51429 | 0.46071 | 39.79% | 92.9% | 0 | 0 | 321.0702 | 1.1579 | 2315.7838 | 54.3006 | 51 | 54 | Copper | 140 | 823.1098 | 8.0747 | 246.933 | 2.4224 | 80.7471 | 3.162 | 0.25532 | 2.6777 | 1.354% | 2042.8189 | 61.2846 | 0.56681 | 0.25175 | 0.27301 |  |  | 0.2859 | 25 | 23.9789 | 20 | 25 | -0.0087578 | -0.042885 | 0 |  | 0 | -0.0087578 | -0.042885 | 0% | 32.88% | 67.12% | -0.031665 | -0.031665 | -1.0555 | -0.1098% | 1.0845 | 729.1026 | 7.1525 | 218.7308 | 2.1457 | 71.525 | 0.22616 | 2.3719 | 0.34128 | 0 | 0.070982 | 17.4667 | 524
11F | Riser to 1st floor | Return | 36 | 0.5 | 108 | 159.6 | 4 | 0 | 0 | 1 | 0 | 10 | 40 | 173.24 | 0.10694 | 173.24 | 4 | 14.4367 | 0.95 | 102.6 | 11.4 | 91.2 | 0.58925 | 3.839% | 0.40714 | 0.3619 | 38.05% | 93.2% | 0 | 0 | 264.44 | 0.95116 | 1902.3129 | 49.2149 | 39 | 42 | Copper | 140 | 2109.2357 | 20.6916 | 84.3694 | 0.82766 | 206.916 | 0.78 | 0.16139 | 0.98906 | 0.4999% | 1194.5896 | 4.7784 | 0.79622 | 0.34082 | 0.36883 |  |  | 0.24076 | 25 | 23.8049 | 20 | 25 | -0.0011509 | -0.0048152 | 0 |  | 0 | -0.011509 | -0.048152 | 1% | 32.55% | 66.45% | -0.0035744 | -0.035744 | -0.8936 | -0.1239% | 0.91661 | 1969.5709 | 19.3215 | 78.7828 | 0.77286 | 193.2149 | 0.15071 | 0.92357 | 0.49327 | 0 | 0.096643 | 13.3933 | 535.7333
12F | Riser to 2nd floor | Return | 24 | 0.5 | 72 | 106.4 | 4 | 0 | 0 | 1 | 0 | 10 | 40 | 138.2608 | 0.12802 | 138.2608 | 4 | 11.5217 | 0.95 | 68.4 | 11.4 | 57 | 0.47027 | 3.207% | 0.27143 | 0.22619 | 32.48% | 92.78% | 0 | 0 | 195.2608 | 0.69647 | 1392.9307 | 42.1134 | 39 | 42 | Copper | 140 | 1184.2745 | 11.6177 | 47.371 | 0.46471 | 116.1773 | 0.78 | 0.090618 | 0.55533 | 0.2807% | 1194.5896 | 4.7784 | 0.58302 | 0.22721 | 0.24672 |  |  | 0.24076 | 25 | 23.2477 | 20 | 25 | -0.0016875 | -0.0048152 | 0 |  | 0 | -0.016875 | -0.048152 | 2% | 32.22% | 65.78% | -0.0037112 | -0.037112 | -0.9278 | -0.1286% | 0.73154 | 1297.0895 | 12.7244 | 51.8836 | 0.50898 | 127.2445 | 0.099251 | 0.60823 | 0.39367 | 0 | 0.070493 | 13.3933 | 535.7333
13F | Riser to 3rd floor | Return | 12 | 0.5 | 36 | 53.2 | 4 | 0 | 0 | 0 | 1 | 10 | 40 | 97.0051 | 0.17964 | 97.0051 | 3 | 8.0838 | 0.95 | 34.2 | 8.55 | 25.65 | 0.32995 | 2.285% | 0.13571 | 0.10179 | 23.58% | 92.05% | 0 | 0 | 122.6551 | 0.43174 | 863.4701 | 33.1573 | 32.6 | 35 | Copper | 140 | 1168.3947 | 11.462 | 46.7358 | 0.45848 | 114.6195 | 1.956 | 0.2242 | 0.68267 | 0.3451% | 834.689 | 3.3388 | 0.51724 | 0.16259 | 0.17873 |  |  | 0.21394 | 25 | 22.3576 | 20 | 25 | -0.0022613 | -0.0042788 | 0 |  | 0 | -0.022613 | -0.042788 | 3% | 31.89% | 65.11% | -0.0035071 | -0.035071 | -0.87677 | -0.1216% | 0.51325 | 1609.5462 | 15.7896 | 64.3818 | 0.63159 | 157.8965 | 0.30885 | 0.94043 | 0.3953 | 0 | 0.059755 | 10.98 | 439.2
14F | Lateral | Return | 6 | 0.5 | 18 | 26.6 | 10 | 0 | 0 | 1 | 0 | 80 | 800 | 70.7904 | 0.35 | 94.5 | 3 | 7.875 | 1 | 18 | 9 | 9 | 0.32143 | 1.173% | 0.071429 | 0.035714 | 10% | 89.04% | 0 | 0 | 103.5 | 0.35714 | 714.2857 | 30.1572 | 26 | 28 | Copper | 140 | 2471.9394 | 24.2497 | 247.1939 | 2.425 | 242.4973 | 0.52 | 0.1261 | 2.5511 | 1.29% | 530.9287 | 5.3093 | 0.67268 | 0.13454 | 0.1523 |  |  | 0.18655 | 25 | 21 | 20 | 25 | -0.0074621 | -0.0093276 | 0 |  | 0 | -0.59697 | -0.74621 | 10% | 29.59% | 60.41% | -0.0078429 | -0.62743 | -0.78429 | -2.175% | 0.5 | 4609.6392 | 45.2206 | 460.9639 | 4.5221 | 452.2056 | 0.23515 | 4.7572 | 0.60541 | 0 | 0.065564 | 5.7133 | 4570.6667
15F | Lateral | Return | 4 | 0.5 | 12 | 17.7333 | 6 | 0 | 0 | 1 | 0 | 80 | 480 | 59.96 | 0.5 | 90 | 2 | 7.5 | 1 | 12 | 6 | 6 | 0.30612 | 0.821% | 0.047619 | 0.02381 | 7.216% | 89.04% | 0 | 0 | 96 | 0.32993 | 659.8639 | 28.9856 | 26 | 28 | Copper | 140 | 2134.5016 | 20.9395 | 128.0701 | 1.2564 | 209.3946 | 0.52 | 0.10889 | 1.3653 | 0.6901% | 530.9287 | 3.1856 | 0.62142 | 0.08969 | 0.10559 |  |  | 0.18655 | 25 | 20.7216 | 20 | 25 | -0.0047888 | -0.0055966 | 0 |  | 0 | -0.38311 | -0.44773 | 15% | 27.95% | 57.05% | -0.0045314 | -0.36251 | -0.75523 | -1.257% | 0.47619 | 4211.3793 | 41.3136 | 252.6828 | 2.4788 | 413.1363 | 0.21483 | 2.6936 | 0.57658 | 0 | 0.052243 | 5.7133 | 2742.4
16F | Lateral | Return | 2 | 0.5 | 6 | 8.8667 | 6 | 0 | 0 | 0 | 1 | 80 | 480 | 46.5672 | 0.8 | 72 | 2 | 6 | 1 | 6 | 6 | 0 | 0.2449 | 0.5131% | 0.02381 | 0 | 0% | 0% | 0 | 0 | 72 | 0.2449 | 489.7959 | 24.9725 | 20 | 22 | Copper | 140 | 4405.2078 | 43.2151 | 264.3125 | 2.5929 | 432.1509 | 1.2 | 0.51858 | 3.1115 | 1.573% | 314.159 | 1.885 | 0.77954 | 0.075788 | 0.093981 |  |  | 0.16237 | 25 | 20 | 20 | 25 | -0.0048711 | -0.0048711 | 0 |  | 0 | -0.38969 | -0.38969 | 20% | 26.3% | 53.7% | -0.0038969 | -0.31175 | -0.64948 | -1.081% | 0.38095 | 9984.7775 | 97.9507 | 599.0867 | 5.877 | 979.5067 | 1.1754 | 7.0524 | 0.77954 | 0 | 0.05584 | 4.4867 | 2153.6
18F | Feed | Return | 1 | 0.5 | 3 | 4.4333 | 8 | 5 | 0 | 0 | 0 | 480 | 3840 | 37.59 | 1 | 45 | 1 | 3.75 | 1 | 3 | 3 | 0 | 0.15306 | 0.4105% | 0.011905 | 0 | 0% | 0% | 0 | 0 | 45 | 0.15306 | 306.1224 | 19.7425 | 13 | 15 | Copper | 140 | 15003.9723 | 147.189 | 1200.3178 | 11.7751 | 1471.8897 | 1.95 | 2.8702 | 14.6453 | 7.403% | 132.7322 | 1.0619 | 1.1532 | 0.08969 | 0.11606 |  |  | 0.13273 | 25 | 20 | 20 | 25 | -0.0053093 | -0.0053093 | 0 |  | 0 | -2.5485 | -2.5485 | 30% | 23.01% | 46.99% | -0.0037165 | -1.7839 | -0.46457 | -6.184% | 0.2381 | 34007.7773 | 333.6163 | 2720.6222 | 26.6893 | 3336.163 | 6.5055 | 33.1948 | 1.1532 | 0 | 0.073883 | 2.0933 | 8038.4
[13 empty] | 12180 | [28 empty] | 124.1007 |  |  | 18.7329 | 197.8336 |  |  | 2238.6476 | 0.51724 |  | 0.63041 | [12 empty] | 47.6856 | 27.94 |  |  |  |  | 28.8486 | [9 empty] | 226.1155 |  |  |  |  | 57916.8
| Dwelling Peak DHW | 45 |  | Kw | [44 empty] | 4471.1722 | 1.1532
| Dwelling Peak CH | 3 |  | Kw | [41 empty] | Building | [24 empty] | 7.6857 | [9 empty] | Building |  |  |  |  | per property
| DP across load (HIU+meter) | 55 |  | kPa | [41 empty] | 114.6971 | [24 empty] | on network | [9 empty] | 176.7293 |  |  |  |  | 120.66
| Peak Load Flow Temperature | 90 |  | C | [41 empty] | kPa | [34 empty] | kPa
| Summer Flow Temperature | 65 |  | C | [66 empty] | 21.1629
| Return DHW | 20 |  | C | [66 empty] | in buildings
| Return CH | 30 |  | C
| Occupants per property | 3
| Flush Rate (HIU function) | 20 |  | l/m
| Peak continuous velocity | 1 |  | m/s
| Heating Season | 120 |  | days
| Fixed DHW/property/day | 35 |  | litres
| DHW/person/day | 20 |  | litres
| DHW Temp Rise (for above) | 40 |  | C
| HIU Standby Temp | 25 |  | C
| HIU Standby Flow | 0 |  | l/hour
| Average tap load | 12 |  | kW
| DHW Priority (0/1) | 1
http://www.katmarsoftware.com/articles/pipe-fitting-pressure-drop.htm
| Descroption | L/D
| Ball valve, full bore | 3
| Ball valve, reduced bore | 25
| Tee, Inline | 20
| Tee, Branch | 60
| 90° screwed elbow | 30
| 90° long radius bend | 13
| 45° screwed elbow | 16
| 45° long radius bend | 10
Note on F7: Used to select appropriate pipe size.
Note on Q7: For calculation of DHW diversity.
Note on R7: The DHW load used in calculation.
Note on T7: Not used in any calculaton
Note on AR7: In a real calculation, pressure calculated pressure drops should be checked against pipe manufacturers pressure drop data.
Note on BD7: Green if under 30s. Yellow if under 60s. With HIU keep warm timed, longer delays are allowable. 1 minute initially selected as maximum allowed time waiting outside keep warm times.
Note on CB7: In a real calculation, pressure calculated pressure drops should be checked against pipe manufacturers pressure drop data.

## Plantroom Sizing
Hour | EST Volume | % | DHW kWh | Max time at peak diversity | Start | End of DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW
1 | 2.25 | 1.828% | 38.8952 | 3.887% | 0:00 | 0:02 | 57.8548 | 0 | -35.1347 | 182.8548 | 0 | -30.2761 | 282.8548 | 0 | -26.3893 | 432.8548 | 0 | -20.559 | 532.8548 | 0 | -16.6721 | 632.8548 | 0 | -12.7853
2 | 1.5 | 1.219% | 25.9301 | 2.591% | 1:00 | 1:02 | 70.8199 | 0 | -23.4231 | 195.8199 | 0 | -20.1841 | 295.8199 | 0 | -17.5928 | 445.8199 | 0 | -13.706 | 545.8199 | 0 | -11.1148 | 645.8199 | 0 | -8.5235
3 | 1.25 | 1.015% | 21.6084 | 2.159% | 2:00 | 2:01 | 75.1416 | 0 | -19.5193 | 200.1416 | 0 | -16.8201 | 300.1416 | 0 | -14.6607 | 450.1416 | 0 | -11.4217 | 550.1416 | 0 | -9.2623 | 650.1416 | 0 | -7.1029
4 | 1 | 0.8123% | 17.2868 | 1.727% | 3:00 | 3:01 | 79.4632 | 0 | -15.6154 | 204.4632 | 0 | -13.4561 | 304.4632 | 0 | -11.7286 | 454.4632 | 0 | -9.1373 | 554.4632 | 0 | -7.4098 | 654.4632 | 0 | -5.6824
5 | 1.6 | 1.3% | 27.6588 | 2.764% | 4:00 | 4:02 | 69.0912 | 0 | -24.9847 | 194.0912 | 0 | -21.5297 | 294.0912 | 0 | -18.7657 | 444.0912 | 0 | -14.6197 | 544.0912 | 0 | -11.8557 | 644.0912 | 0 | -9.0918
6 | 2.1 | 1.706% | 36.3022 | 3.628% | 5:00 | 5:02 | 60.4478 | 0 | -32.7924 | 185.4478 | 0 | -28.2577 | 285.4478 | 0 | -24.63 | 435.4478 | 0 | -19.1884 | 535.4478 | 0 | -15.5607 | 635.4478 | 0 | -11.9329
7 | 5.5 | 4.468% | 95.0772 | 9.501% | 6:00 | 6:06 | 1.6728 | 0 | -85.8848 | 126.6728 | 0 | -74.0083 | 226.6728 | 0 | -64.5071 | 376.6728 | 0 | -50.2553 | 476.6728 | 0 | -40.7541 | 576.6728 | 0 | -31.253
8 | 10.7 | 8.692% | 184.9683 | 18.48% | 7:00 | 7:11 | -88.2183 | 0 | -167.0849 | 36.7817 | 0 | -143.9798 | 136.7817 | 0 | -125.4956 | 286.7817 | 0 | -97.7695 | 386.7817 | 0 | -79.2853 | 486.7817 | 0 | -60.8012
9 | 9.3 | 7.555% | 160.7669 | 16.07% | 8:00 | 8:10 | -64.0169 | -88.2183 | -233.4417 | 60.9831 | 0 | -125.1413 | 160.9831 | 0 | -109.0757 | 310.9831 | 0 | -84.9772 | 410.9831 | 0 | -68.9115 | 510.9831 | 0 | -52.8459
10 | 7.5 | 6.093% | 129.6507 | 12.96% | 9:00 | 9:08 | -32.9007 | -152.2352 | -269.3508 | 92.0993 | 0 | -100.9204 | 192.0993 | 0 | -87.9642 | 342.0993 | 0 | -68.53 | 442.0993 | 0 | -55.5738 | 542.0993 | 0 | -42.6177
11 | 6.7 | 5.443% | 115.8213 | 11.57% | 10:00 | 10:07 | -19.0713 | -185.1359 | -289.7591 | 105.9287 | 0 | -90.1556 | 205.9287 | 0 | -78.5814 | 355.9287 | 0 | -61.2201 | 455.9287 | 0 | -49.646 | 555.9287 | 0 | -38.0718
12 | 5.9 | 4.793% | 101.9919 | 10.19% | 11:00 | 11:06 | -5.2419 | -204.2071 | -296.3381 | 119.7581 | 0 | -79.3907 | 219.7581 | 0 | -69.1985 | 369.7581 | 0 | -53.9103 | 469.7581 | 0 | -43.7181 | 569.7581 | 0 | -33.5259
13 | 5.2 | 4.224% | 89.8911 | 8.983% | 12:00 | 12:05 | 6.8589 | -209.449 | -290.6492 | 131.8589 | 0 | -69.9715 | 231.8589 | 0 | -60.9885 | 381.8589 | 0 | -47.5141 | 481.8589 | 0 | -38.5312 | 581.8589 | 0 | -29.5482
14 | 4.4 | 3.574% | 76.0617 | 7.601% | 13:00 | 13:05 | 20.6883 | -202.5902 | -271.298 | 145.6883 | 0 | -59.2066 | 245.6883 | 0 | -51.6057 | 395.6883 | 0 | -40.2043 | 495.6883 | 0 | -32.6033 | 595.6883 | 0 | -25.0024
15 | 3.8 | 3.087% | 65.6897 | 6.564% | 14:00 | 14:04 | 31.0603 | -181.9019 | -241.2405 | 156.0603 | 0 | -51.133 | 256.0603 | 0 | -44.5685 | 406.0603 | 0 | -34.7219 | 506.0603 | 0 | -28.1574 | 606.0603 | 0 | -21.5929
16 | 3.9 | 3.168% | 67.4184 | 6.737% | 15:00 | 15:04 | 29.3316 | -150.8416 | -211.7417 | 154.3316 | 0 | -52.4786 | 254.3316 | 0 | -45.7414 | 404.3316 | 0 | -35.6356 | 504.3316 | 0 | -28.8984 | 604.3316 | 0 | -22.1612
17 | 4.5 | 3.656% | 77.7904 | 7.774% | 16:00 | 16:05 | 18.9596 | -121.51 | -191.7793 | 143.9596 | 0 | -60.5522 | 243.9596 | 0 | -52.7785 | 393.9596 | 0 | -41.118 | 493.9596 | 0 | -33.3443 | 593.9596 | 0 | -25.5706
18 | 6.5 | 5.28% | 112.3639 | 11.23% | 17:00 | 17:07 | -15.6139 | -102.5504 | -204.0506 | 109.3861 | 0 | -87.4643 | 209.3861 | 0 | -76.2357 | 359.3861 | 0 | -59.3927 | 459.3861 | 0 | -48.164 | 559.3861 | 0 | -36.9353
19 | 9.5 | 7.717% | 164.2242 | 16.41% | 18:00 | 18:10 | -67.4742 | -118.1643 | -266.5107 | 57.5258 | 0 | -127.8325 | 157.5258 | 0 | -111.4214 | 307.5258 | 0 | -86.8047 | 407.5258 | 0 | -70.3935 | 507.5258 | 0 | -53.9824
20 | 9 | 7.311% | 155.5808 | 15.55% | 19:00 | 19:09 | -58.8308 | -185.6385 | -326.1772 | 66.1692 | 0 | -121.1045 | 166.1692 | 0 | -105.5571 | 316.1692 | 0 | -82.236 | 416.1692 | 0 | -66.6886 | 516.1692 | 0 | -51.1412
21 | 7.5 | 6.093% | 129.6507 | 12.96% | 20:00 | 20:08 | -32.9007 | -244.4693 | -361.5849 | 92.0993 | 0 | -100.9204 | 192.0993 | 0 | -87.9642 | 342.0993 | 0 | -68.53 | 442.0993 | 0 | -55.5738 | 542.0993 | 0 | -42.6177
22 | 6 | 4.874% | 103.7206 | 10.36% | 21:00 | 21:06 | -6.9706 | -277.37 | -371.0625 | 118.0294 | 0 | -80.7363 | 218.0294 | 0 | -70.3714 | 368.0294 | 0 | -54.824 | 468.0294 | 0 | -44.4591 | 568.0294 | 0 | -34.0941
23 | 4.5 | 3.656% | 77.7904 | 7.774% | 22:00 | 22:05 | 18.9596 | -284.3406 | -354.6099 | 143.9596 | 0 | -60.5522 | 243.9596 | 0 | -52.7785 | 393.9596 | 0 | -41.118 | 493.9596 | 0 | -33.3443 | 593.9596 | 0 | -25.5706
24 | 3 | 2.437% | 51.8603 | 5.182% | 23:00 | 23:03 | 44.8897 | -265.381 | -312.2272 | 169.8897 | 0 | -40.3682 | 269.8897 | 0 | -35.1857 | 419.8897 | 0 | -27.412 | 519.8897 | 0 | -22.2295 | 619.8897 | 0 | -17.0471
1 | [7 empty] | -220.4913 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
2 | [7 empty] | -162.6365 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 | [7 empty] | -91.8166 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 | [7 empty] | -16.6751 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
6 | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
7 | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
8 | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Total | 123.1 | 100% | 2128 | [5 empty] | 1 |  |  | 1.1 |  |  | 1.2 |  |  | 1.3 |  |  | 1.4 |  |  | 1.5
DHW kW |  |  | 88.6667 | [5 empty] | 1125 | kW |  | 1250 |  |  | 1350 |  |  | 1500 |  |  | 1600 |  |  | 1700
Heating kW |  |  | 1028.25 | [5 empty] | 96.75 | kW |  | 221.75 |  |  | 321.75 |  |  | 471.75 |  |  | 571.75 |  |  | 671.75
Minimum Boiler Power |  |  | 1116.9167
[9 empty] | -371.0625 | kWh |  | -143.9798 |  |  | -125.4956 |  |  | -97.7695 |  |  | -79.2853 |  |  | -60.8012
Selected Boiler Power | [8 empty] | 5300.8929 | litres |  | 2056.8538 |  |  | 1792.7949 |  |  | 1396.7065 |  |  | 1132.6475 |  |  | 868.5885
Spare for DHW
Min kWh
Central Buffer Volume
| Boiler Size | Buffer Size
| 1125 | 5300.8929
| 1250 | 2056.8538
| 1350 | 1792.7949
| 1500 | 1396.7065
| 1600 | 1132.6475
| 1700 | 868.5885
Note on E22: Calculted hourly volumes from EST Data weightings
Note on F22: With a known volume per hour, and a peak diversified flow, the maximum possible draw off is the hourly volume drawn in a single hit at full diversity.

## Pipes
Diameter | Wal | Bore | Material | Roughness Constant | Tube Thermal Conductivity | Insulation Thermal Conductivity | Cost | ro | ri | Insulation Thickness, Flow | rs | Thermal Loss, Flow | Insulation Thickness, Return | rs | Thermal Loss, Return
mm | mm | mm |  |  | W/mk | W/mK | £/m |  |  | mm |  | W/m/K | mm |  | W/m/K
10 | 0.8 | 8.4 | Copper | 140 | 401 | 0.034 | 1.6784 | 0.005 | 0.0042 | 50 | 0.055 | 0.089089 | 30 | 0.035 | 0.10978
12 | 0.8 | 10.4 | Copper | 140 | 401 | 0.034 | 2 | 0.006 | 0.0052 | 50 | 0.056 | 0.095643 | 30 | 0.036 | 0.11923
15 | 1 | 13 | Copper | 140 | 401 | 0.034 | 2.0933 | 0.0075 | 0.0065 | 50 | 0.0575 | 0.10488 | 30 | 0.0375 | 0.13273
22 | 1 | 20 | Copper | 140 | 401 | 0.034 | 4.4867 | 0.011 | 0.01 | 50 | 0.061 | 0.12471 | 30 | 0.041 | 0.16237
28 | 1 | 26 | Copper | 140 | 401 | 0.034 | 5.7133 | 0.014 | 0.013 | 50 | 0.064 | 0.14056 | 30 | 0.044 | 0.18655
35 | 1.2 | 32.6 | Copper | 140 | 401 | 0.034 | 10.98 | 0.0175 | 0.0163 | 50 | 0.0675 | 0.15825 | 30 | 0.0475 | 0.21394
42 | 1.5 | 39 | Copper | 140 | 401 | 0.034 | 13.3933 | 0.021 | 0.0195 | 50 | 0.071 | 0.17537 | 30 | 0.051 | 0.24076
54 | 1.5 | 51 | Copper | 140 | 401 | 0.034 | 17.4667 | 0.027 | 0.0255 | 50 | 0.077 | 0.20385 | 30 | 0.057 | 0.2859
75 | 1.5 | 72 | Steel | 140 | 401 | 0.034 | 25 | 0.0375 | 0.036 | 50 | 0.0875 | 0.25213 | 30 | 0.0675 | 0.36344
100 | 1.5 | 97 | Steel | 140 | 401 | 0.034 | 33.3333 | 0.05 | 0.0485 | 50 | 0.1 | 0.3082 | 30 | 0.08 | 0.45452
150 | 1.5 | 147 | Steel | 140 | 401 | 0.034 | 50 | 0.075 | 0.0735 | 50 | 0.125 | 0.4182 | 30 | 0.105 | 0.6349
200 | 1.5 | 197 | Steel | 140 | 401 | 0.034 | 66.6667 | 0.1 | 0.0985 | 50 | 0.15 | 0.52687 | 30 | 0.13 | 0.81424
250 | 1.5 | 247 | Steel | 140 | 401 | 0.034 | 83.3333 | 0.125 | 0.1235 | 50 | 0.175 | 0.6349 | 30 | 0.155 | 0.9931
http://www.engineeringtoolbox.com/conductive-heat-loss-cylinder-pipe-d_1487.html
[16 empty] | 10 | 123
Q = (ti - to) / [(ln(ro / ri) / 2 π k L) + (ln(rs / ro) / 2 π ks L)] | [15 empty] | 20 | 75
[16 empty] | 30 | 59
http://www.insulationgiant.co.uk/Rockwool-Heating-and-Ventilation-Pipe-Insulation-40mm-Wall-Thickness/p/9000094465 | [15 empty] | 40 | 50
[16 empty] | 50 | 44
[16 empty] | 60 | 41
[16 empty] | 70 | 38
[16 empty] | 80 | 36
[16 empty] | 90 | 34
[16 empty] | 100 | 32
Note on I2: Based on quoted prices for 100m lengths

## Energy Use
| Power |  | Hours/Year | Annual Energy
Losses in Buildings | 21.1629 | kW | 8760 | 185386.6762 | kWh
Losses in Network | 7.6857 | kW | 8760 | 67326.7014 | kWh
Domestic Hot Water |  |  |  | 776720 | kWh
Central Heating | 1080 | kW | 600 | 648000 | kWh

## Energy Generation
Heat Source Efficiency
Chart of Boiler Efficiency at different Flow Temperatures
Peak Load Flow Temperature | 90 | C
Summer Flow Temperature | 65 | C
Return Summer | 20 | C | [11 empty] | `
Return Winter | 25.4521 | C
Percentage Input for each temp range
Temperature | Fuel Price | Carbon Kg CO2/kWh | Peak | 20 | 30 | 40 | 50 | 55 | 60 | 70 | 80 | 90 | 100 |  | Percent Input | 20 | 30 | 40 | 50 | 55 | 60 | 70 | 80 | 90 | Percent Input | 20 | 30 | 40 | 50 | 55 | 60 | 70 | 80 | 90
Gas Boiler | 0.03 | 0.18 | 90 | 95% | 95% | 95% | 95% | 90% | 90% | 88% | 85% | 80% |  |  | 76.31% | 0% | 0% | 0% | 0% | 0% | 24.76% | 25.32% | 26.22% | 0% | 32.15% | 0% | 0% | 0% | 0% | 0% | 32.15% | 0% | 0% | 0%
Heat Pump | 0.11 | 0.5 | 55 | 500% | 450% | 400% | 300% | 150% | [6 empty] | 23.69% | 2.027% | 4.952% | 5.571% | 3.714% | 7.429% | 0% | 0% | 0% | 0% | 67.85% | 11.58% | 12.86% | 14.47% | 9.646% | 19.29% | 0% | 0% | 0% | 0%
Max |  |  |  | 500% | 450% | 400% | 300% | 150% | 90% | 88% | 85% | 80%
Carbon |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.18 | 0.18 | 0.18 | 0.18
|  |  |  | Heat Pump | Heat Pump | Heat Pump | Heat Pump | Heat Pump | Gas Boiler | Gas Boiler | Gas Boiler | Gas Boiler
Winter Full Load
Energy Input |  |  |  | 20% | 22.22% | 25% | 33.33% | 66.67% | 111.1% | 113.6% | 117.6% | 125%
Degrees Input |  |  |  | 4.5479 | 10 | 10 | 5 | 5 | 10 | 10 | 10 | 0
Degrees Input, check max |  |  |  | 4.5479 | 10 | 10 | 5 | 5 | 10 | 10 | 10 | 0
Total | [12 empty] | 64.5479
Percent of Load |  |  |  | 7.046% | 15.49% | 15.49% | 7.746% | 7.746% | 15.49% | 15.49% | 15.49% | 0%
Percentage Energy Input of Total Load |  |  |  | 1.409% | 3.443% | 3.873% | 2.582% | 5.164% | 17.21% | 17.6% | 18.23% | 0%
Total Input as percentage of output | ` | [11 empty] | 69.52%
Overall Efficiency | [12 empty] | 143.9% | Efficiency
Percentage Input |  |  |  | 2.027% | 4.952% | 5.571% | 3.714% | 7.429% | 24.76% | 25.32% | 26.22% | 0%
Check = 100 | [12 empty] | 100%
Carbon |  |  |  | 0.010136 | 0.024762 | 0.027857 | 0.018572 | 0.037143 | 0.044572 | 0.045585 | 0.047194 | 0
Carbon Average | [12 empty] | 0.25582 | Kg CO2/kWh input
[13 empty] | 0.17784 | Kg CO2/kWh LOAD
Summer
Energy Input |  |  |  | 20% | 22.22% | 25% | 33.33% | 66.67% | 111.1% | 113.6% | 117.6% | 125%
Degrees Input |  |  |  | 10 | 10 | 10 | 5 | 5 | 5 | -5 | -15 | -25
Degrees Input, check max |  |  |  | 10 | 10 | 10 | 5 | 5 | 5 | 0 | 0 | 0
Total | [12 empty] | 45
Percent of Load |  |  |  | 22.22% | 22.22% | 22.22% | 11.11% | 11.11% | 11.11% | 0% | 0% | 0%
Percentage Energy Input of Total Load |  |  |  | 4.444% | 4.938% | 5.556% | 3.704% | 7.407% | 12.35% | 0% | 0% | 0%
Total Input as percentage of output | ` | [11 empty] | 38.4%
Overall Efficiency | [12 empty] | 260.5% | Efficiency
Percentage Input |  |  |  | 11.58% | 12.86% | 14.47% | 9.646% | 19.29% | 32.15% | 0% | 0% | 0%
Check = 100 | [12 empty] | 100%
Carbon |  |  |  | 0.057878 | 0.064309 | 0.072347 | 0.048232 | 0.096463 | 0.057878 | 0 | 0 | 0
Carbon Average | [12 empty] | 0.39711 | Kg CO2/kWh input
[13 empty] | 0.15247 | Kg CO2/kWh LOAD